## Sheet1
Status | Process ID | Requester Name | Position Name | Notif SAP No | Notif Date | Notif Type | Notif Short Text | Priority | Remark History | Reported By | Planner Group | Required Start Date | Required End Date | Downtime Start Date | Downtime End Date | Total Downtime | Total Down Minutes | Total Downtime in HR | Discover | Symptom | Efect | Main Work Center | Order No | Order Superior | Order Type | Order Priority | Short.Desc.Order | Function Location Code | Function Location Desc | Equipment Code | Equipment Desc | Planning Start Date | Plan Finish Date | PM Act Type | System Condition | Budget Source | Actual Cost | Total Estimated Cost | Internal Cost | Total Service Cost | Total Material Cost Actual | Total Planned Cost | Reservation No | PR No | CODE | Object Parts | CODE | Object Part Damage | CODE | Object Part Cause | CODE | Action Plan | TECO | TECO DATE | CCTR CODE | CCTR DESC | OBJTYPE_ID | OBJTYPE
| 3570839 | Yossie Listeana Sari | SSE INSTRUMENT ADMINISTRATION |  | 41758 | M1 | LINE TUBING DISCH POMPA BOCOR | Urgent | 16/05/2014 14:17 Yossie Listeana Sari : Line Tubing Discharge pompa bocor Mengganti line tubing Disch pompa dengan tubing baru done by : Widodo & A. Syarnubi | A. Syarnubi | N01 - SSE Instrumentation | 41758.3333 | 41758.4167 | 41758.3646 | 41758.3854 | 0 | 30 | 0.5 | Maintenance Technician | Instrumentation Problem | No effect | INSTTECH |  |  | EP01 | Urgent | REPAIR CHEMICAL PUMP DEMULSIFIER MANIFOL | EP-A01A-05-FLSTA-FLST_A-PIPE-MNFOLD_01 | SSE-JENE-FIELD STATION#A-MANIFOLD#01 | G-A01A05046 | PNEUMATIC INJECTOR MANIFOLD LP | 29/04/2014 | 41675 | Corrective | 0 | A010-A05-202070:Jene Instrumentation A010070305 (A010070305) | 0 | 0 | 61.13 | 0 | 61.13 | 61.13 |  |  | CDVC | Control Device | LEAK | Leak (Bocor) | COTH | Other (explain in text) | REPL | Replacing |  |  |  |  | CHEMPUMP | CHEMICAL PUMP
| 3570775 | Yossie Listeana Sari | SSE INSTRUMENT ADMINISTRATION |  | 41788 | M1 | CHEMICAL PUMP TIDAK PEKERJA | Urgent | 16/05/2014 13:39 Yossie Listeana Sari : Ada kebocoran sedikit pada pompa, Pompa chemical tidak bekerja Check pompa, spring patah, sementara diganti dengan spring bekas yang ada di shop Test Function : ok done by : Widodo & A. Syarnubi | A. Syarnubi | N01 - SSE Instrumentation | 41758.3333 | 41758.3542 |  |  |  |  | 0 | Maintenance Technician | Instrumentation Problem | No effect | INSTTECH |  |  | EP01 | Urgent | REPLACE SPRING CHEMICAL PUMP | EP-A01A-05-FLSTA-FLST_A-VSEL-FWKO_04 | SSE-JENE-FIELD STATION #A-FWKO #04 | G-A01A05050 | PNEUMATIC INJECTOR#4 FWKO JENE | 29/04/2014 | 41675 | Corrective | 0 | A010-A05-202070:Jene Instrumentation A010070305 (A010070305) | 0 | 0 | 20 | 0 | 20 | 20 |  |  | CDVC | Control Device | LEAK | Leak (Bocor) | COTH | Other (explain in text) | REPL | Replacing |  |  |  |  | CHEMPUMP | CHEMICAL PUMP
| 3570678 | Opry | SSE PUMP & DIESEL SHOP ADMINISTRATION |  | 41774.3333 | M1 | PERBAIKAN UNIT AUTOCAR 71-327 | Essential | 16/05/2014 11:11 Opry : Akan dilakukan perbaikan unit autocar 71-327.Diperlukan penggantian spare part:End Tierod left autocar,End tierod right autocar,Valve assy quick release.Part tersebut ada di WHS Soka | Desra K | M01 - SSE Mechanical | 41774.3333 | 41774.6667 | 41774.3333 | 41774.6667 | 8 | 0 | 8 | Maintenance Technician | Mechanical Problem | Non Productive Time | PUMPMECH |  |  | EP01 | Essential | PERBAIKAN UNIT AUTOCAR 71-327 | EP-A01A-05-EQUIP-DLSHOP-TRUK-HTRUCK_GR | SSE-JENE-DIESEL SHOP-HEAVY TRUCK GROUP | HE-A01A05007 | AUTOCAR OFB | 16/05/2014 | 30/05/2014 | Corrective | 0 | A010-A05-201100:Jene Transp.Land.M. A010070405 (A010070405) | 0 | 703.68 | 0 | 0 | 0 | 703.68 |  |  | VLVE | Valve | WORN | Worn Out (Aus) | CMLT | Design Life Time of material | REPL | Replacing |  |  |  |  | HEAVYTRUCK | HEAVY TRUCK
| 3570677 | Yossie Listeana Sari | SSE INSTRUMENT ADMINISTRATION |  | 41733 | Z7 | RELOKASI TCS DARI WELL MATRA | Essential | 16/05/2014 11:11 Yossie Listeana Sari : Diperlukan TCS untuk mengetahui water cut oil yang khusus dari Well Matra ke Matra temp done by : Widodo & Yantoro | Widodo K | N01 - SSE Instrumentation | 41733 | 41733 |  |  |  |  | 0 |  |  | -- select -- | INSTTECH |  |  | EP05 | Essential | RELOKASI TRUE CUT SAMPLER MATRA | EP-A01A-12-FLSTA-STAT_A-LINE-P_LINE_01 | SSE-MATRA -PIPE LINE TO MATRA RECEIVING | S-A01A12001 | TRUECUT SAMPLE MATRA | 41733 | 41947 | Modification | 1 | A010-A12-202071:Matra Instrumentation A010070305 (A010070305) | 0 | 0 | 710.32 | 0 | 710.32 | 710.32 | [14 empty] | TOOLS | TOOLS
| 3570623 | Yossie Listeana Sari | SSE INSTRUMENT ADMINISTRATION |  | 41766 | M1 | ALARM HIGH LIQUID SUCTION STAGE#01 | Urgent | 16/05/2014 10:39 Yossie Listeana Sari : Troubleshooting Comp#04, Alarm High Liquid Scrubber Suction stage#01 indikasi Floater terlepas Release Pressure Scrubber, Check Floater, dilakukan penggantian Floater (Level switch) Test Running Comp#04, ok done by : Rahmat & Agus K | Agus K | N01 - SSE Instrumentation | 41766.3125 | 41766.4167 |  |  |  |  | 0 | Maintenance Technician | Instrumentation Problem | Non Productive Time | INSTTECH |  |  | EP01 | Urgent | TROUBLESHOTING COMP#04 SOKA | EP-A01A-06-GPLNT-GPLN_A-COMP-GASCOM_04 | SSE-SOKA-GAS PLANT#A-GAS COMPRESSOR #04 | K-A04A09032-INSSYS | INSTRUMENT SYSTEM COMPRESSOR GAS | 41825 | 41917 | Corrective | 0 | A010-A06-202070:Soka Instrumentation A010070305 (A010070305) | 0 | 0 | 753.6 | 0 | 753.6 | 753.6 |  |  | ISYS | Instrument Control System | JAMM | Jammed (Macet) | COTH | Other (explain in text) | RPAI | Repairing |  |  |  |  | INSTSYSTEM | INSTRUMENT SYSTEM
| 3570569 | Yossie Listeana Sari | SSE INSTRUMENT ADMINISTRATION |  | 41753 | M1 | FILTER IAS POMPA COTRON PECAH | Urgent | 16/05/2014 10:16 Yossie Listeana Sari : Dilakukan penggantian Filter baru done by : Widodo & Syarnubi | A. Syarnubi | N01 - SSE Instrumentation | 41753 | 41753 |  |  |  |  | 0 | Maintenance Technician | Instrumentation Problem | Non Productive Time | INSTTECH |  |  | EP01 | Urgent | REPLACE FILTER IAS POMPA COTRON | EP-A01A-05-FLSTA-FLST_A-PIPE-DISCH_WIP | SSE-JENE-FIELD STATION#A-DISCHARGE WIP | G-A01A05045 | PNEUMATIC INJECTOR DISC WIP#2 | 24/04/2014 | 27/04/2014 | Corrective | 0 | A010-A05-202070:Jene Instrumentation A010070305 (A010070305) | 0 | 0 | 500 | 0 | 500 | 500 |  |  | CDVC | Control Device | BROK | Broken (Patah) | COTH | Other (explain in text) | REPL | Replacing |  |  |  |  | CHEMPUMP | CHEMICAL PUMP
| 3570510 | Yossie Listeana Sari | SSE INSTRUMENT ADMINISTRATION |  | 41741 | M1 | ADANYA KEBOCORAN LIQUID PADA STEM LCV | Urgent | 16/05/2014 09:55 Yossie Listeana Sari : Adanya kebocoran Liquid pada stem LCV Scrubber HP Teras Shutdown LCV, Release Liquid, Modifikasi seal untuk stem LCV Test Normally function, status : ok done by : Suhadi & Agus K | Agus K | N01 - SSE Instrumentation | 41741 | 41741 |  |  |  |  | 0 | Maintenance Technician | Instrumentation Problem | No effect | INSTTECH |  |  | EP01 | Urgent | MODIFIKASI SEAL STEM LCV | EP-A01A-03-FLSTA-FLST_A-VSEL-SCRBR_08 | SSE-TERAS-FIELD STATION-VESEL-SCRUBBER#8 | D-A01A03017-INSYS | FUEL GAS SCRUBBER MBFT-XXX INSTRUMENT | 41977 | 15/04/2014 | Corrective | 0 | A010-A03-202070:Teras Instrumentation A010070305 (A010070305) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CNVV | Control Valve (Press, Temp, Flow, Level) | LEAK | Leak (Bocor) | COTH | Other (explain in text) | RPAI | Repairing |  |  |  |  | INSTSYSTEM | INSTRUMENT SYSTEM
| 3570453 | Yossie Listeana Sari | SSE INSTRUMENT ADMINISTRATION |  | 41755 | M1 | TURBINE METER TIDAK MERECORD | Urgent | 16/05/2014 09:42 Yossie Listeana Sari : Turbine meter tidak merecord Totalizernya mati dilakukan penggantian Turbine meter , Housing & Totalizer K Factor yng baru : 941.28 done by : Nico & Yantoro | Nico SJ | N01 - SSE Instrumentation | 41755.5417 | 41755.6042 |  |  |  |  | 0 | Maintenance Technician | Instrumentation Problem | Non Productive Time | INSTTECH |  |  | EP01 | Urgent | REPLACE TURBINE & TOTALIZER | EP-A01A-03-FLSTA-FLST_A-VSEL-SPRTOR_04 | SSE-TERAS-FIELD STATION-VESEL-TEST SEP | D-A01A03004-FC | TEST SEP MBDT-104 LOOP FLOW | 26/04/2014 | 29/04/2014 | Corrective | 0 | A010-A03-202070:Teras Instrumentation A010070305 (A010070305) | 0 | 0 | 2971.7 | 0 | 2971.7 | 2971.7 |  |  | CTRL | Controller (Press, Temp, Flow, Level) | JAMM | Jammed (Macet) | COTH | Other (explain in text) | REPL | Replacing |  |  |  |  | LOOPFLOW | LOOP FLOW
| 3570409 | Yossie Listeana Sari | SSE INSTRUMENT ADMINISTRATION |  | 41771 | M1 | RANGE PRESS GAUGE KEBESARAN | Urgent | 16/05/2014 09:28 Yossie Listeana Sari : Press gauge yang terpasang rangenya terlalu besar 0-1000 sedangkan Operating Pressure berada diantara 50-70 psi dilakukan penggantian Press gauge dengan range 0-100 psi done by Nico & Yantoro | Nico SJ | N01 - SSE Instrumentation | 41771 | 41771 |  |  |  |  | 0 | Maintenance Technician | Instrumentation Problem | Quality Degradation | INSTTECH |  |  | EP01 | Urgent | REPLACE PRESS GAUGE SCRUBBER FUEL KONENG | EP-A01A-20-FLSTA-FLST_A-VSEL-SCRBR_03 | SSE-KONENG-FIELD STAT#A-SCRUB FUEL GAS | D-A01A20009-PC | SCRUBBER MBF-113 LOOP PRESS | 41978 | 15/05/2014 | Corrective | 0 | A010-A20-202070:Koneng Instrumentation A010070305 (A010070305) | 0 | 0 | 126.55 | 0 | 126.55 | 126.55 |  |  | GAUG | Gauge | IMBL | Imbalance (Tidak Balance) | COTH | Other (explain in text) | REPL | Replacing |  |  |  |  | LOOPPRESUR | LOOP PRESSURE
| 3570378 | Yossie Listeana Sari | SSE INSTRUMENT ADMINISTRATION |  | 41771 | M1 | DISPLAY TURBINE METER MATI | Urgent | 16/05/2014 09:16 Yossie Listeana Sari : Closing Temuan Condition monitoring Dilakukan penggantian Batre Turbine meter done by : Nico & Yantoro | Nico SJ | N01 - SSE Instrumentation | 41771.6458 | 41771.6667 |  |  |  |  | 0 | Maintenance Technician | Instrumentation Problem | Non Productive Time | INSTTECH |  |  | EP01 | Urgent | PENGGANTIAN BATRE TURBINE METER PUMPING | EP-A01A-20-FLSTA-FLST_A-PIPE-PIPE_PUMP01 | SSE-KONENG-FIELD STAT#A-PIPING PUMP | PL-A01A20003-INSYS | INSTRUMENT TRANS PUMPS PAX-310/311 | 41978 | 15/05/2014 | Condition Monitoring | 0 | A010-A20-202070:Koneng Instrumentation A010070305 (A010070305) | 0 | 0 | 8000 | 0 | 8000 | 8000 |  |  | CTRL | Controller (Press, Temp, Flow, Level) | JAMM | Jammed (Macet) | CMLT | Design Life Time of material | REPL | Replacing |  |  |  |  | INSTSYSTEM | INSTRUMENT SYSTEM
| 3570085 | Opry | SSE PUMP & DIESEL SHOP ADMINISTRATION |  | 41768.4167 | M1 | BOCOR MECHSEAL WIP #06 JENE | Essential | 15/05/2014 22:22 Opry : Terjadi kebocoran di Unit pompa WIP #06 Bagian DE.Dilakukan penggantian mechseal karena mengalami kebocoran.Dilakukan Allignment ( Data Terlampir ).Test Run load dipressure 1100 Psi dan Ampere 320 Psi.Kondisi unit normal.done by hkm,sst | Hengky M | M03 - SSE Pump | 41768.4167 | 41768.7083 | 41768.4167 | 41768.7083 | 7 | 0 | 7 | Personal on duty (operator/checker) | Mechanical Problem | Non Productive Time | PUMPMECH |  |  | EP01 | Essential | BOCOR MECHSEAL WIP #06 JENE | EP-A01A-05-FLSTA-PUMP_A-PUMP-WIPUMP_06 | SSE-JENE-WATER INJECTION PUMP #06 | G-A01A05029 | PUMP IR 4x10CS-6 WATER INJECTION | 41887 | 41887 | Corrective | 0 | A010-A05-201111:Jene Pumping A010070206 (A010070206) | 0 | 7503 | 0 | 0 | 0 | 7503 |  |  | MSEL | Mechanical Seal Assembly | LEAK | Leak (Bocor) | CMLT | Design Life Time of material | REPL | Replacing |  |  |  |  | CENTRIPUMP | CENTRIFUGAL PUMP
| 3569836 | Rita Agustina | SSE PLANNER | [14 empty] | 0 |  |  |  |  | 7300049245 |  | EP03 | Essential | INSP TRAFO PT-A04A12001 TR PLNT_A 1 PGB | EP-A01A-14-BOOST-PLNT_A-XMER-TRANSF_01 | SSE-PENGABUAN-TRANSFORMATOR #01 | PT-A04A12001 | TRANSFORMER | 28/05/2014 | 28/05/2014 | Inspection | 1 | A010-A14-201021:Pengabuan Electrical - A010070202 (A010070202) | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | TRANSFORMR | TRANSFORMER
| 3569835 | Rita Agustina | SSE PLANNER | [14 empty] | 0 |  |  |  |  | 7300049224 |  | EP03 | Essential | PM2(1YR) MTRACOMKM-A01A09005 GPLNT_A1GKB | EP-A01A-09-GPLNT-GPLN_A-COMP-AIRCOM_01 | SSE-GUNUNG KEMBANG-AIR COMPRESSOR #01 | KM-A01A09005 | ELMOT EUROMOTOR 11 KW AIR COMP DRIVER | 30/05/2014 | 31/05/2014 | Preventive Maintenance | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | ELECTMOTOR | ELECTRIC MOTOR
| 3569834 | Rita Agustina | SSE PLANNER | [14 empty] | 0 |  |  |  |  | 7300049174 |  | EP03 | Essential | INSP 2K ELMOT GM-A01A14005 WIP#07 JENE | EP-A01A-05-FLSTA-PUMP_A-PUMP-WIPUMP_07 | SSE-JENE-WATER INJECTION PUMP #07 | GM-A01A14005 | ELMOT RELIANCE 350 HP CTP DRIVER | 28/05/2014 | 28/05/2014 | Inspection | 1 | A010-A05-201020:Jene Electrical - A010070202 (A010070202) | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | ELECTMOTOR | ELECTRIC MOTOR
| 3569827 | Opry | SSE PUMP & DIESEL SHOP ADMINISTRATION |  | 41773.4167 | M1 | SERVICE RIG IDECO 5 | Essential | 15/05/2014 11:54 Opry : Akan dilakukan PM Unit RIG Ideco 5,sehingga diperlukan penggantian spare part. 1.Pump steering 2.Valve Brake 3.Valve Safety 4.Valve Relax 5.Seal Oil part tersebut akan diambil dari logistik Soka | Desra | M02 - SSE Diesel & Rig | 41773.4167 | 41773.7083 | 41773.4167 | 41773.7083 | 7 | 0 | 7 | Maintenance Technician | Mechanical Problem | Non Productive Time | PUMPMECH |  |  | EP01 | Essential | SERVICE RIG IDECO 5 | EP-A01A-06-WOWSS-RIGG_A-ENGN-ENGINE_01 | SSE-SOKA-IDECO_5-MOBILE-ENGINE #01 | RIG-A04A09005-E1 | ENGINE DIESEL GM 8V71 MOBILE DRIVER | 15/05/2014 | 29/05/2014 | Predictive Maintenance | 0 | A010-A06-201190:Soka WO/WS Rig A010060205 (A010060205) | 0 | 4470.6 | 0 | 0 | 0 | 4470.6 |  |  | VLVE | Valve | WORN | Worn Out (Aus) | CMLT | Design Life Time of material | REPL | Replacing |  |  |  |  | DISLENGINE | DIESEL ENGINE
| 3569783 | Opry | SSE PUMP & DIESEL SHOP ADMINISTRATION |  | 41770.2917 | M1 | REPAIR CTP #02 TERAS | Urgent | 15/05/2014 10:51 Opry : Dilakukan dismantle CTP #02 Teras karena akan dilakukan repair di SHop Jene.Setelah repair akan pompa tersebut akan diinstall di CTP #01 Matra Temporary.done by tom,pay | Toni M | M03 - SSE Pump | 41770.2917 | 41771.7083 | 41770.2917 | 41771.7083 | 34 | 0 | 34 | Maintenance Technician | Mechanical Problem | Non Productive Time | PUMPMECH |  |  | EP01 | Urgent | REPAIR CTP #02 TERAS | EP-A01A-03-FLSTA-PUMP_A-PUMP-CTPUMP_02 | SSE-TERAS-CRUDE TRANSFER PUMP #02 | G-A01A03002 | PUMP GASO 1550 CRUDE TRANSFER | 15/05/2014 | 22/05/2014 | Corrective | 0 | A010-A03-201111:Teras Pumping A010070206 (A010070206) | 0 | 1302.04 | 0 | 0 | 0 | 1302.04 |  |  | LNER | Liner | WORN | Worn Out (Aus) | CMLT | Design Life Time of material | REPL | Replacing |  |  |  |  | RECIPRPUMP | RECIPROCATING PUMP
| 3569582 | Opry | SSE PUMP & DIESEL SHOP ADMINISTRATION |  | 41764.625 | M1 | REPLACE ROD PISTON CTP #04 MATRA | Urgent | 14/05/2014 22:11 Opry : Terjadi kebocoran packing rod pada unit CTP #04.Kemudian dilakukan pengecekan dan ditemukan: -Rod Piston dalam keadaan tergores -Rubber piston sudah rusak -Packing rod max adjust man Kemudian dilakukan penggantian part tersebut .Unit test run load dalam kondisi normal dan tidak ada kebocoran lagi.done by uchu,hdy | Uchu Agus | M03 - SSE Pump | 41764.625 | 41765.4583 | 41764.625 | 41765.4583 | 20 | 0 | 20 | Maintenance Technician | Mechanical Problem | Non Productive Time | PUMPMECH |  |  | EP01 | Urgent | REPLACE ROD PISTON CTP #04 MATRA | EP-A01A-12-FLSTA-PUMP_A-PUMP-CTPUMP_04 | SSE-MATRA TEMP-CRUDE TRANSFER PUMP #04 | G-A01B05012 | PUMP GASO 1753 CRUDE TRANSFER | 41764 | 41795 | Corrective | 0 | A010-A12-201111:Matra PumpingA010070206 (A010070206) | 0 | 1806.4 | 0 | 0 | 0 | 1806.4 |  |  | RPST | Rubber Piston | WORN | Worn Out (Aus) | CMLT | Design Life Time of material | REPL | Replacing |  |  |  |  | RECIPRPUMP | RECIPROCATING PUMP
| 3569579 | Opry | SSE MECHANICAL ADMINISTRATION | 6200004188 | 41771.3854 | M2 | WHITE SMOKE FROM MUFFLER GENSET #01 PGB | Emergency | 14/05/2014 21:24 Opry : Unit down dengan no indikasi.Saat akan dirun load kembali ditemukan: - asap putih keluar dari muffler. - Turbocharge left bocor ring shaft oil. - kebocoran oil pada front cover aux pump. Action: -Penggantian turbo left assy new -Replace seal front cover aux pump -cleaning spark plug cylinder 6 & 8 .Unit run load kembali pukul 17.15 WIB.Done by aco,krj | Africo | M01 - SSE Mechanical | 41771.3854 | 41771.7188 | 41771.3854 | 41771.7188 | 8 | 0 | 8 | Personal on duty (operator/checker) | Mechanical Problem | Non Productive Time & Env | MECHTECH | 7200005861 |  | EP02 | Emergency | WHITE SMOKE FROM MUFFLER GENSET #01 PGB | EP-A01A-14-BOOST-PLNT_A-GSET-GENSET_01 | SSE-PENGABUAN-POWER PLANT-GENSET #01 | PE-A01A00002 | ENGINE CAT G3512 GENERATOR DRIVER | 41978 | 41978 | Breakdown | 0 | A010-A14-201031:Pengabuan Power Plant - A010070203 (A010070203) | 0 | 0 | 2495.24 | 0 | 2495.24 | 2495.24 |  |  | TURB | Turbocharger | LEAK | Leak (Bocor) | COOD | Operation Beyond Design | REPL | Replacing |  |  | A010070203 | Power Plant | GASENGINE | GAS ENGINE
| 3569249 | Opry | SSE PUMP & DIESEL SHOP ADMINISTRATION |  | 41770.2917 | M1 | REPAIR CTP #02 TERAS | Desireable | 14/05/2014 14:54 Opry : Dilakukan dismantle CTP #02 Teras karena akan dilakukan repair di SHop Jene.Setelah repair akan pompa tersebut akan diinstall di CTP #01 Matra Temporary.done by tom,pay | Toni M | M03 - SSE Pump | 41770.2917 | 41771.7083 | 41770.2917 | 41771.7083 | 34 | 0 | 34 | Maintenance Technician | Mechanical Problem | Non Productive Time | PUMPMECH |  |  | EP01 | Desireable | REPAIR CTP #02 TERAS | EP-A01A-03-FLSTA-PUMP_A-PUMP-CTPUMP_02 | SSE-TERAS-CRUDE TRANSFER PUMP #02 | G-A01A03002 | PUMP GASO 1550 CRUDE TRANSFER | 14/05/2014 | 21/05/2014 | Corrective | 0 | A010-A03-201111:Teras Pumping A010070206 (A010070206) | 0 | 1302.04 | 0 | 0 | 0 | 1302.04 |  |  | LNER | Liner | WORN | Worn Out (Aus) | CMLT | Design Life Time of material | REPL | Replacing |  |  |  |  | RECIPRPUMP | RECIPROCATING PUMP
| 3568954 | Opry | SSE PUMP & DIESEL SHOP ADMINISTRATION |  | 41773.4583 | M1 | PROBLEM FEEDER #03 PENGABUAN | Urgent | 14/05/2014 11:41 Opry : Info dari operator Pengabuan Booster tanggal 12 may 2014: - Ada bunyi kasar pada bagian bearing pompa ( Noise ) - Tanggal 13 May 2014 mekanik melakukan pengecekan pada unit Feeder #03 Pengabuan.Temuan:Shaft pompa putus,hub coupling rusak,grid coupling patah. - Unit akan dibawa ke Jene untuk dilakukan perbaikan. | Toni M | M03 - SSE Pump | 41773.4583 | 41773.7083 | 41773.4583 | 41773.7083 | 6 | 0 | 6 | Personal on duty (operator/checker) | Abnormal Noise | Non Productive Time | PUMPMECH |  |  | EP01 | Urgent | PROBLEM FEEDER #03 PENGABUAN | EP-A01A-14-BOOST-BOOS_A-PUMP-FDPUMP_03 | SSE-PENGABUAN-FEEDER PUMP #03 | G-A01A14008 | PUMP GOULDS 3196 MT FEEDER TRANSFER | 14/05/2014 | 14/05/2014 | Corrective | 0 | A010-A14-201111:Pengabuan Pumping & Gauging A010070206 (A010070206) | 0 | 947.92 | 0 | 0 | 0 | 947.92 |  |  | SHFT | Shaft | WORN | Worn Out (Aus) | CMLT | Design Life Time of material | REPL | Replacing |  |  |  |  | CENTRIPUMP | CENTRIFUGAL PUMP
| 3567468 | Rison | SSE PUMP & DIESEL SHOP ADMINISTRATION | 6100017512 | 41772.6667 | M1 | PENGGANTIAN LINER & PISTON CTP#01 RBT | Urgent | 13/05/2014 09:35 Rison : Akan dilakukan penggantian liner dan piston 4 1/2 inch pada CTP#01 Rambutan, dikarenakan part rusak. | Toni M | M03 - SSE Pump | 41771.4167 | 41771.5 | 41771.4167 | 41771.5 | 2 | 0 | 2 | Maintenance Technician | Mechanical Problem | Non Productive Time | PUMPMECH | 7100015532 |  | EP01 | Urgent | PENGGANTIAN LINER & PISTON CTP#01 RBT | EP-A01A-02-FLSTA-PUMP_A-PUMP-CTPUMP_01 | SSE-RAMBUTAN-CRUDE TRANSFER PUMP #01 | G-A01A02001 | PUMP GASO 1700 CRUDE TRANSFER | 13/05/2014 | 19/05/2014 | Corrective | 0 | A010-A02-201111:Rambutan Pumping A010070206 (A010070206) | 216 | 216 | 0 | 0 | 216 | 216 | 271122 |  | RPST | Rubber Piston | BROK | Broken (Patah) | CMLT | Design Life Time of material | REPL | Replacing |  |  | A010070206 | Pump Shop | RECIPRPUMP | RECIPROCATING PUMP
| 3567468 | Rison | SSE PUMP & DIESEL SHOP ADMINISTRATION | 6100017512 | 41772.6667 | M1 | PENGGANTIAN LINER & PISTON CTP#01 RBT | Urgent | 13/05/2014 09:35 Rison : Akan dilakukan penggantian liner dan piston 4 1/2 inch pada CTP#01 Rambutan, dikarenakan part rusak. | Toni M | M03 - SSE Pump | 41771.4167 | 41771.5 | 41771.4167 | 41771.5 | 2 | 0 | 2 | Maintenance Technician | Mechanical Problem | Non Productive Time | PUMPMECH | 7100015532 |  | EP01 | Urgent | PENGGANTIAN LINER & PISTON CTP#01 RBT | EP-A01A-02-FLSTA-PUMP_A-PUMP-CTPUMP_01 | SSE-RAMBUTAN-CRUDE TRANSFER PUMP #01 | G-A01A02001 | PUMP GASO 1700 CRUDE TRANSFER | 13/05/2014 | 19/05/2014 | Corrective | 0 | A010-A02-201111:Rambutan Pumping A010070206 (A010070206) | 216 | 216 | 0 | 0 | 216 | 216 | 271122 |  | RPST | Rubber Piston | BROK | Broken (Patah) | CMLT | Design Life Time of material | REPL | Replacing |  |  | A010070206 | Pump Shop | RECIPRPUMP | RECIPROCATING PUMP
| 3565708 | Rison | SSE MECHANICAL ADMINISTRATION | 6100017510 | 41770 | M1 | KEBOCORAN PADA PRELUBE PUMP COMP#03 TRS | Urgent | 11/05/2014 21:52 Rison : Pada saat PM 1500 engine gas comp#03 teras ditemukan kebocoran oil pada prelube pompa dan shaft idle gear. Dilakukan rekondisi pada prelube pump dan reseal pada shaft idle gear. Test run load Ok. | Paramarta BW | M01 - SSE Mechanical | 41740.375 | 41740.8333 | 41740.375 | 41740.8333 | 11 | 0 | 11 | Maintenance Technician | Leakage | Non Productive Time | MECHTECH | 7100015530 |  | EP01 | Urgent | KEBOCORAN PADA PRELUBE PUMP COMP#03 TRS | EP-A01A-03-GPLNT-GPLN_A-COMP-GASCOM_03 | SSE-TERAS-GAS PLANT#A-GAS COMPRESSOR #03 | KE-A01A03005 | ENGINE CAT G3512 COMPRESSOR DRIVER | 41948 | 18/05/2014 | Corrective | 0 | A010-A03-201152:Teras Gas Compression (A010241000) | 0 | 0 | 431.76 | 0 | 431.76 | 431.76 |  |  | ORNG, GSKT | O-Ring, Gasket | LEAK, LEAK | Leak (Bocor), Leak (Bocor) | CMLT, CMLT | Design Life Time of material, Design Life Time of material | REPL, REPL | Replacing, Replacing |  |  | A010241000 | Sep/Deh.Plant - Gas | GASENGINE | GAS ENGINE
| 3565400 | Edy Syazali | SSE INSTRUMENT PLANNER TECH. | 6300032029 | 41789.0003 | M3 | CAL 3 MONTH FLOWMETER JUMPER BORANG | Essential |  | DENI FERDIANSYAH | N01 - SSE Instrumentation | 41789 | 41789.9993 |  |  |  |  | 0 |  |  |  | INSTTECH | 7300049239 |  | EP03 | Essential | CAL 3 MONTH FLOWMETER JUMPER BORANG | EP-A01A-16-FLSTA-STAT_A-LINE-PIG_RECEIVR | SSE-BORANG-PIPE LINE-PIG RECEIVER | S-A01A16002-FC | PIG RECEIVER-LOOP FLOW | 30/05/2014 | 30/05/2014 | Calibration | 0 | A010-A16-202071:Borang Instrumentation A010070305 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070305 | Instrumentation | LOOPFLOW | LOOP FLOW
| 3565399 | Edy Syazali | SSE INSTRUMENT PLANNER TECH. | 6300032037 | 41787.0003 | M3 | PROVING (MONTHLY) PD METER#2 PENGABUAN | Essential |  | DENI FERDIANSYAH | N01 - SSE Instrumentation | 41787 | 41787.9993 |  |  |  |  | 0 |  |  |  | INSTTECH | 7300049232 |  | EP03 | Essential | PROVING (MONTHLY) PD METER#2 PENGABUAN | EP-A01A-14-BOOST-BOOS_A-RECR-METER_01 | SSE-PENGABUAN-BOOS#A-METER#01 | FQI-A04A12001-FC6 | PD METER SMITH 2 | 28/05/2014 | 28/05/2014 | Inspection | 1 | A010-A14-202071:Pengabuan Instrumentation A010070305 (A010070305) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070305 | Instrumentation | LOOPFLOW | LOOP FLOW
| 3565393 | Edy Syazali | SSE INSTRUMENT PLANNER TECH. | 6300032040 | 41789.0003 | M3 | CAL 3 MONTH GAS CHROMATOGRAPH BORANG | Essential |  | DENI FERDIANSYAH | N01 - SSE Instrumentation | 41789 | 41789.9993 |  |  |  |  | 0 |  |  |  | INSTTECH | 7300049225 |  | EP03 | Essential | CAL 3 MONTH GAS CHROMATOGRAPH BORANG | EP-A01A-16-FLSTA-STAT_A-RECR-METER_002 | SSE-BORANG-GAS FLOW RECORDER #02 | FR-A01A16002-UV | GAS METER SYS #02 ANALIZER GC | 30/05/2014 | 30/05/2014 | Calibration | 1 | A010-A16-202071:Borang Instrumentation A010070305 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070305 | Instrumentation | ANALYZER | ANALYZER
| 3565381 | Edy Syazali | SSE INSTRUMENT PLANNER TECH. | 6300032042 | 41789.0003 | M3 | CAL 3 MONTH FLOWMETER#2 DARAT BORANG | Essential |  | DENI FERDIANSYAH | N01 - SSE Instrumentation | 41789 | 41789.9993 |  |  |  |  | 0 |  |  |  | INSTTECH | 7300049208 |  | EP03 | Essential | CAL 3 MONTH FLOWMETER#2 DARAT BORANG | EP-A01A-16-FLSTA-STAT_A-RECR-METER_002 | SSE-BORANG-GAS FLOW RECORDER #02 | FR-A01A16002-FC1 | GAS METER SYS #02 LOOP FLOW 2 | 30/05/2014 | 30/05/2014 | Calibration | 1 | A010-A16-202071:Borang Instrumentation A010070305 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070305 | Instrumentation | LOOPFLOW | LOOP FLOW
| 3565380 | Edy Syazali | SSE INSTRUMENT PLANNER TECH. | 6300032050 | 41789.0003 | M3 | CAL 3 MONTH FLOWMETER#1 DARAT BORANG | Essential |  | DENI FERDIANSYAH | N01 - SSE Instrumentation | 41789 | 41789.9993 |  |  |  |  | 0 |  |  |  | INSTTECH | 7300049207 |  | EP03 | Essential | CAL 3 MONTH FLOWMETER#1 DARAT BORANG | EP-A01A-16-FLSTA-STAT_A-RECR-METER_002 | SSE-BORANG-GAS FLOW RECORDER #02 | FR-A01A16002-FC | GAS METER SYS #02 LOOP FLOW 1 | 30/05/2014 | 30/05/2014 | Calibration | 1 | A010-A16-202071:Borang Instrumentation A010070305 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070305 | Instrumentation | LOOPFLOW | LOOP FLOW
| 3565379 | Edy Syazali | SSE INSTRUMENT PLANNER TECH. | 6300032041 | 41789.0003 | M3 | CAL 3 MONTH FLOWMETER#2 APUNG BORANG | Essential |  | DENI FERDIANSYAH | N01 - SSE Instrumentation | 41789 | 41789.9993 |  |  |  |  | 0 |  |  |  | INSTTECH | 7300049206 |  | EP03 | Essential | CAL 3 MONTH FLOWMETER#2 APUNG BORANG | EP-A01A-16-FLSTA-STAT_A-RECR-METER_001 | SSE-BORANG-GAS FLOW RECORDER #01 | FR-A01A16001-FC1 | GAS METER SYS #01 LOOP FLOW 2 | 30/05/2014 | 30/05/2014 | Calibration | 0 | A010-A16-202071:Borang Instrumentation A010070305 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070305 | Instrumentation | LOOPFLOW | LOOP FLOW
| 3565378 | Edy Syazali | SSE INSTRUMENT PLANNER TECH. | 6300032049 | 41789.0003 | M3 | CAL 3 MONTH FLOWMETER#1 APUNG BORANG | Essential |  | DENI FERDIANSYAH | N01 - SSE Instrumentation | 41789 | 41789.9993 |  |  |  |  | 0 |  |  |  | INSTTECH | 7300049205 |  | EP03 | Essential | CAL 3 MONTH FLOWMETER#1 APUNG BORANG | EP-A01A-16-FLSTA-STAT_A-RECR-METER_001 | SSE-BORANG-GAS FLOW RECORDER #01 | FR-A01A16001-FC | GAS METER SYS #01 LOOP FLOW 1 | 30/05/2014 | 30/05/2014 | Calibration | 0 | A010-A16-202071:Borang Instrumentation A010070305 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070305 | Instrumentation | LOOPFLOW | LOOP FLOW
| 3565377 | Edy Syazali | SSE INSTRUMENT PLANNER TECH. | 6300032038 | 41787.0003 | M3 | PROVING (MONTHLY) PD METER#1 PENGABUAN | Essential |  | DENI FERDIANSYAH | N01 - SSE Instrumentation | 41787 | 41787.9993 |  |  |  |  | 0 |  |  |  | INSTTECH | 7300049204 |  | EP03 | Essential | PROVING (MONTHLY) PD METER#1 PENGABUAN | EP-A01A-14-BOOST-BOOS_A-RECR-METER_01 | SSE-PENGABUAN-BOOS#A-METER#01 | FQI-A04A12001-FC5 | PD METER SMITH 1 | 28/05/2014 | 28/05/2014 | Inspection | 1 | A010-A14-202071:Pengabuan Instrumentation A010070305 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070305 | Instrumentation | LOOPFLOW | LOOP FLOW
| 3565072 | Otto Ariendra | SSE PLANNER SHE | [14 empty] | 0 |  |  |  |  | 7300049345 |  | EP03 | Essential | PM 6MONTH APAB 150LBS KONENG | EP-A01A-20 | SSE-KONENG |  |  | 41917 | 41917 | Preventive Maintenance | 0 | A010-A20-201292:Koneng Fire Safety - A010140100 ( A010020300 ) | 0 | 0 | 0 | 0 | 0 | 0
| 3564619 | Heriyanto | SSE INSTRUMENT ADMINISTRATION | 6100017508 | 41750 | M1 | REPAIR TURBINE METER SEP TEST JENE | Essential | 09/05/2014 15:33 Heriyanto : Totalizer turbine meter mati . check batree drop , ganti batree yang baru , chek setting k factor yang diinput 100 seharusnya k factor yg bner adalah 7896 , ganti k factor , dan test function ok . dilakukan oleh widodo dan ahmad syarnubi pada tgl 21 april 14. | Widodo | N01 - SSE Instrumentation | 41750.7083 | 41750.75 |  |  | 0 | 0 | 0 | Personal on duty (operator/checker) | Abnormal Flow | Quality Degradation | INSTTECH | 7100015528 |  | EP01 | Essential | REPAIR TURBINE METER SEP TEST JENE | EP-A01A-05-FLSTA-FLST_A-VSEL-SPRTOR_04 | SSE-JENE-FIELD STAT#A-TEST SEPARATOR #01 | D-A01A05006-FC | SEPARATOR CDX 71921 LOOP FLOW | 21/04/2014 | 21/04/2014 | Corrective | 0 | A010-A05-202070:Jene Instrumentation A010070305 (A010070305) | 0 | 0 | 75 | 0 | 75 | 75 |  |  | RECR | Recorder (Press, Temp, Flow, Level) | DEFF | Defective (Cacat) | COTH | Other (explain in text) | CHEK, REPL, PROG | Checking, Replacing, Programming |  |  | A010070305 | Instrumentation | LOOPFLOW | LOOP FLOW
| 3564599 | Heriyanto | SSE INSTRUMENT ADMINISTRATION | 6100017507 | 41759 | M1 | REPAIR CHEMICAL PUMP COTRON JENE | Essential | 09/05/2014 15:19 Heriyanto : Pump chemical tidak berfungsi , dikarenkaan suction pump tidak menghisap . check slang suction pump , banyak kotoran dari tedmon chemical , check scrubber chemical banyak kotoran , dibersihkan semua lumut dalam scrubber test pump . ok dilakukan oleh widodo dan sahmad syanubi pada tanggal 30 april 14. | Widodo | N01 - SSE Instrumentation | 41759.5833 | 41759.625 |  |  | 0 | 0 | 0 | Personal on duty (operator/checker) | Abnormal Flow | Quality Degradation | INSTTECH | 7100015527 |  | EP01 | Essential | REPAIR CHEMICAL PUMP COTRON JENE | EP-A01A-05-FLSTA-FLST_A-PIPE-DISCH_WIP | SSE-JENE-FIELD STATION#A-DISCHARGE WIP | G-A01A05042 | PHENEUMATIC INJECTOR CHEMICAL | 30/04/2014 | 30/04/2014 | Corrective | 1 | A010-A05-202070:Jene Instrumentation A010070305 (A010070305) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | ISYS | Instrument Control System | DIRT | Dirty (Kotor) | COTH | Other (explain in text) | CHEK, CLEN, TEST | Checking, Cleaning, Testing |  |  | A010070305 | Instrumentation | CENTRIPUMP | CENTRIFUGAL PUMP
| 3564544 | Heriyanto | SSE INSTRUMENT ADMINISTRATION | 6700000492 | 41750 | Z7 | ACTIVASI TCS NON JENE | Essential | 09/05/2014 15:01 Heriyanto : Aktifasi kembali pump tcs non Jene , Repair pump yamada pump s5tuck , install ias untuk pump yamada ,tesct function ok . | WIDODO | N01 - SSE Instrumentation | 41750.4375 | 41780.7292 |  |  | 0 | 0 | 0 |  |  | -- select -- | INSTTECH | 7500001002 |  | EP05 | Essential | ACTIVASI TCS NON JENE | EP-A01A-05-FLSTA-FLST_A-PIPE-FLOW_SOKA | SSE-JENE-FIELD STAT#A-PIPING FROM SOKA | S-A01A05001 | TRUECUT SAMPLE JENE | 21/04/2014 | 21/04/2014 | Modification | 1 | A010-A05-202070:Jene Instrumentation A010070305 (A010070305) | 0 | 0 | 778.33 | 0 | 778.33 | 778.33 | [14 empty] | TOOLS | TOOLS
| 3564377 | Rison | SSE MECHANICAL ADMINISTRATION | 6400004833 | 41768.5417 | Z4 | TACHOMETER & PROTECTION OVERSPEED ENGINE | Urgent | 09/05/2014 13:41 Rison : Dibutuhkan Tachometer dan protection overspeed gas engine untuk kebutuhan Engine di area Matra, Serdang dan Gunung kembang. | Eko Yulianto | M01 - SSE Mechanical | 41768 | 41768 |  |  | 0 | 0 | 0 |  |  | -- select -- | MECHTECH | 7400007223 |  | EP04 | Urgent | TACHOMETER & PROTECTION OVERSPEED ENGINE | EP-A01A-04-BOOST-BOOS_A-PUMP | PUMP |  |  | 41887 | 41862 | Non Plant Equipment | 1 | A010-A04-201111:Serdang Pumping A010070206 (A010070206) | 0 | 6400 | 0 | 0 | 0 | 6400 | 270872 | [11 empty] | A010070206 | Pump Shop
| 3564258 | Heriyanto | SSE INSTRUMENT ADMINISTRATION | 6700000490 | 41740 | Z7 | INSTALL METER BARTON JUMPER INDRALAYA | Urgent | 09/05/2014 11:07 Heriyanto : Meter barton dicuri , sehingga perlu dipasang kembali . Dan tlah dilakukan instalasi meter recorder pada tanggal 11 april 14. olrh widodo dan edy Yantoro . | Widodo | N01 - SSE Instrumentation | 41740.375 | 41740.5 |  |  | 0 | 0 | 0 |  |  | -- select -- | INSTTECH | 7500001000 |  | EP05 | Urgent | INSTALL METER BARTON JUMPER INDRALAYA | EP-A01A-18-FLSTA-STAT_A-JUMP-PKBUNG | SSE-INDRA LAYA-JUMPER PAYAKABUNG | PL-A01A18001-FC | JUMP PAYAKABUNG LOOP FLOW | 14/04/2014 | 14/04/2014 | Equipment exchange | 1 | A010-A18-202070:Indralaya Instrumentation A010070305 (A010070305) | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | LOOPFLOW | LOOP FLOW
| 3563710 | Rison | SSE PUMP & DIESEL SHOP ADMINISTRATION |  | 41765.6667 | Z4 | BATTERY LOW VOLTAGE DARLEY F.PUMP META | Urgent | 08/05/2014 21:53 Rison : Battery darley fire pump meta low voltage, dilakukan penggantian battery 70 AH. Pada saat engine running idle ada abnormal noise pada engine. Dilakukan pengecekan dengan melepas housing coupling dan didapat suri coupling dan suri shaft pompa sudah aus. Install housing coupling, test run dengan Rpm diatas 1000 Rpm abnormal noise hilang, Test pump Ok. | Bambang E.Y | M01 - SSE Mechanical | 41764.3333 | 41765.6667 |  |  |  |  | 0 |  |  | -- select -- | PUMPMECH |  |  | EP04 | Urgent | BATTERY LOW VOLTAGE DARLEY F.PUMP META | EP-A01A-23-FLSTA-PUMP_A-PUMP-FRPUMP_01 | SSE-META-FIRE HYDRANT PUMP #01 |  |  | 41856 | 41831 | Non Plant Equipment | 1 |  | 0 | 0 | 0 | 0 | 0 | 0
| 3563511 | Heriyanto | SSE INSTRUMENT ADMINISTRATION | 6100017501 | 41736 | M1 | REPAIR TCS PUMPING RAMBUTAN | Essential | 08/05/2014 16:01 Heriyanto : Motor TCS Tidak berfungsi ( motor stuck ) . Disconect power , chek power pada MCB , Repair dan cleaning Motor ( motor korosi ) , dan function test motor , sttus OK . Dilakukan oleh suhadi dan agus k pada tanggal 7 april 14. | Suhadi | N01 - SSE Instrumentation | 41736 | 41736 |  |  | 0 | 0 | 0 | Personal on duty (operator/checker) | Abnormal Power | No effect | INSTTECH | 7100015521 |  | EP01 | Essential | REPAIR TCS PUMPING RAMBUTAN | EP-A01A-02-FLSTA-FLST_A-PIPE-PIPE_PUMP | SSE-RBT-FIELD STATION#A-PIPING TRAN PUMP | S-A01A02001 | TRUECUT SAMPLE RAMBUTAN | 41824 | 41824 | Corrective | 1 | A010-A02-202070:Rambutan Instrumentation A010070305 (A010070305) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | RECR | Recorder (Press, Temp, Flow, Level) | CORR | Corroded (Korosi) | COTH | Other (explain in text) | CHEK, CLEN, TEST | Checking, Cleaning, Testing |  |  | A010070305 | Instrumentation | TOOLS | TOOLS
| 3563476 | Heriyanto | SSE INSTRUMENT ADMINISTRATION | 6100017502 | 41736 | M1 | REPAIR TRU CUT SAMPLE RAMBUTAN | Urgent | 08/05/2014 15:38 Heriyanto : True cut sample tidak berfungsi , liquid tidak masuk ke tabung TCS . Close valve , check regulator ( adanya sumbatan dan kotoran didalam regulator , cleaning dan test normally function , status OK . | Suhadi | N01 - SSE Instrumentation | 41736 | 41736 |  |  | 0 | 0 | 0 | Personal on duty (operator/checker) | Abnormal Flow | No effect | INSTTECH | 7100015522 |  | EP01 | Urgent | REPAIR TRU CUT SAMPLE RAMBUTAN | EP-A01A-02-FLSTA-FLST_A-PIPE-PIPE_PUMP | SSE-RBT-FIELD STATION#A-PIPING TRAN PUMP | S-A01A02001 | TRUECUT SAMPLE RAMBUTAN | 41824 | 41824 | Corrective | 1 | A010-A02-202070:Rambutan Instrumentation A010070305 (A010070305) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | RECR | Recorder (Press, Temp, Flow, Level) | CLOG | Clogged / Blocked (Tersumbat) | COTH | Other (explain in text) | CHEK, CLEN, TEST | Checking, Cleaning, Testing |  |  | A010070305 | Instrumentation | TOOLS | TOOLS
| 3563430 | Heriyanto | SSE INSTRUMENT ADMINISTRATION | 6700000491 | 41756 | Z7 | RECONDITION LINE IAS PCV CTP JENE | Essential | 08/05/2014 15:10 Heriyanto : Line IAS PCV Recylce pumping ctp menghalangi pipa 16 , dilkukan modifikasi IAS PCV Recycle pumping CTP . Dilakukan oleh Widodo , dan Nubi pada tanggal 27 april 14 . | Widodo | N01 - SSE Instrumentation | 41756 | 41756 |  |  | 0 | 0 | 0 |  |  | -- select -- | INSTTECH | 7500001001 |  | EP05 | Essential | RECONDITION LINE IAS PCV CTP JENE | EP-A01A-05-FLSTA-FLST_A-PIPE-DISCH_CTP | SSE-JENE-FIELD STATION#A-DISCHARGE CTP | PL-A01A05002-PC | PIPE CTP DISCH. LOOP PRESS | 27/04/2014 | 27/04/2014 | Modification | 1 | A010-A05-202070:Jene Instrumentation A010070305 (A010070305) | 0 | 581.71 | 0 | 0 | 0 | 581.71 | 270900 | [13 empty] | LOOPPRESUR | LOOP PRESSURE
| 3561283 | Rison | SSE PUMP & DIESEL SHOP ADMINISTRATION | 6100017503 | 41745.9167 | M1 | ENGINE NO START AUTOCAR TRACTOR | Urgent | 06/05/2014 21:29 Rison : Pada saat akan menstart engine, pada electric starter tidak mau memutar pada electric starter, lepas kabel battery. Replace electric starter dan cable serta replace battery. Test run Ok. | Bambang E.Y | M01 - SSE Mechanical | 41745.7083 | 41745.9167 | 41745.7083 | 41745.9167 | 5 | 0 | 5 | Maintenance Technician | Electrical Problem | Non Productive Time & Env | PUMPMECH | 7100015523 |  | EP01 | Urgent | ENGINE NO START AUTOCAR TRACTOR | EP-A01A-05-EQUIP-DLSHOP-TRUK-HTRUCK_GR | SSE-JENE-DIESEL SHOP-HEAVY TRUCK GROUP | HE-A01A05008 | AUTOCAR TRACTOR | 41856 | 15/05/2014 | Corrective | 0 | A010-A05-201100:Jene Transp.Land.M. A010070405 (A010070405) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | STRT | Starter | JAMM | Jammed (Macet) | CMLT | Design Life Time of material | REPL | Replacing |  |  | A010070405 | Transp.Land.M | HEAVYTRUCK | HEAVY TRUCK
| 3561281 | Rison | SSE PUMP & DIESEL SHOP ADMINISTRATION | 6100017484 | 41742.5417 | M1 | ENGINE LOW POWER WHEEL LOADER | Essential | 06/05/2014 21:19 Rison : Engine low power, dilakukan pengecekan pada fuel filter dan muffler. Ditemukan fuel filter secondary dan primery sangat kotor dan bercampur air, sehingga engine running hunting. Dan pada mufler ditemukan kebocoran. fule filter diganti dan muffler dilas, kondisi unit run Ok. | Bambang E.Y | M01 - SSE Mechanical | 41742.5417 | 41742.625 | 41742.5417 | 41742.625 | 2 | 0 | 2 | Personal on duty (operator/checker) | Mechanical Problem | Non Productive Time & Env | PUMPMECH | 7100015504 |  | EP01 | Essential | ENGINE LOW POWER WHEEL LOADER | EP-A01A-05-EQUIP-DLSHOP-CONS-LOADER _GR | SSE-JENE-DIESEL SHOP-WHEEL LOADER GROUP | HE-A01A05001 | WHEEL LOADER 950B | 41795 | 14/05/2014 | Corrective | 0 | A010-A05-201090:Jene Heavy Equipment A010070403 (A010070403) | 0 | 0 | 44.18 | 0 | 44.18 | 44.18 |  |  | FLFT, MUFL | Fuel Filter, Muffler | DIRT, BROK | Dirty (Kotor), Broken (Patah) | COOD, CMLT | Operation Beyond Design, Design Life Time of material | REPL, WELD | Replacing, Welding |  |  | A010070403 | Heavy Equipment | LOADER | LOADER
| 3561193 | Rison | SSE PUMP & DIESEL SHOP ADMINISTRATION | 6100017485 | 41752.6667 | M1 | BATTERY LOW VOLTAGE F.HYDRANT 01 PGB | Urgent | 06/05/2014 16:49 Rison : Pada saat engine mau di start, ditemukan battery low voltage, dilakukan pengukuran battery nol volt. battery di charger selama 1 jam, tetapi saat di start battery masih low voltage. Dilakukan penggantian baattery dengan yang baru. Setelah itu dilakukan pengecekan pada unit, ditemukan kebocoran dari gasket cylinder head dan cover belting motor tidak ada, perlu dibuatkan. | Edison | M01 - SSE Mechanical | 41752.5417 | 41752.6667 | 41752.5417 | 41752.6667 | 3 | 0 | 3 | Personal on duty (operator/checker) | Electrical Problem | Non Productive Time & Env | PUMPMECH | 7100015505 |  | EP01 | Urgent | BATTERY LOW VOLTAGE F.HYDRANT 01 PGB | EP-A01A-14-BOOST-BOOS_A-PUMP-FRPUMP_01 | SSE-PENGABUAN-FIRE PUMP #01 | GE-A01A04008 | ENGINE FORD 2725E FIRE WATER PUMP DRIVER | 41795 | 13/05/2014 | Corrective | 0 | A010-A14-201111:Pengabuan Pumping & Gauging A010070206 (A010070206) | 0 | 0 | 396.44 | 0 | 396.44 | 396.44 |  |  | ESYS | Electrical Control System | SHCR | Short-Circuited | COOD | Operation Beyond Design | REPL | Replacing |  |  | A010070206 | Pump Shop | DISLENGINE | DIESEL ENGINE
| 3560933 | Rison | SSE MECHANICAL ADMINISTRATION | 6400004830 | 41757.5417 | Z4 | LEAK HOSE AIR COMP#A KERAMASAN | Desireable | 06/05/2014 14:02 Rison : Tanggal 6 februari 2014 dilakukan perbaikan air compressor, dilakukan penggantian hose assembly dan dilakukan monitoring. Dari hasil inspeksi beberapa part membutuhkan segera penggantian karena sudah hampir mencapai MTBF nya. | Tri Chayono | L01 - SSE Electrical | 41676.375 | 41676.6667 |  |  | 0 | 0 | 0 |  |  | -- select -- | MECHTECH | 7400007220 |  | EP04 | Desireable | LEAK HOSE AIR COMP#A KERAMASAN | EP-A01A-21-FLSTA-FLST_A-COMP-AIRCOMP_01 | SSE-KERAMASAN-AIR COMPRESSOR #01 | K-A01A21001 | COMPRESSOR mfg?? AIR SUPPLY | 41795 | 30/11/2014 | Non Plant Equipment | 1 | A010-A21-201162:Keramasan Pumping & Gauging - A010070206 (A010070206) | 0 | 12090.45 | 0 | 0 | 0 | 12090.45 | 270762 | [11 empty] | A010070206 | Pump Shop | AIRCOMPRES | AIR COMPRESSOR
| 3560146 | Rita Agustina | SSE PLANNER | 6300032010 | 41785.0003 | M3 | PM1 1500h GEN PG-A01A05002 LU#01 IBUL | Essential | 06/05/2014 10:10 Rita Agustina : For Rh 55500 | HENDRO ANGGORO | L01 - SSE Electrical | 41785 | 41785.9993 |  |  |  |  | 0 |  |  |  | ELECTECH | 7300049226 |  | EP03 | Essential | PM1 1500h GEN PG-A01A05002 LU#01 IBUL | EP-A01A-01-PPLNT-PLNT_A-GSET-GENSET_01 | SSE-IBUL-GENERATOR SET #01 | PG-A01A05002 | GENERATOR CAT SR4 POWER PLAN | 26/05/2014 | 26/05/2014 | Preventive Maintenance | 0 | A010-A01-201031:Ibul Power Plant A010070203 (A010070203) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070203 | Power Plant | GENERATOR | GENERATOR
| 3560143 | Rita Agustina | SSE PLANNER | 6300032012 | 41789.0003 | M3 | PM1(4M) MTR ACOM KM-A01A09001 PPLN 1 GKB | Essential | 06/05/2014 14:31 Rita Agustina : Timebase | HENDRO ANGGORO | L01 - SSE Electrical | 41789 | 41789.9993 |  |  |  |  | 0 |  |  |  | ELECTECH | 7300049217 |  | EP03 | Essential | PM1(4M) MTR ACOM KM-A01A09001 PPLN 1 GKB | EP-A01A-09-PPLNT-PLNT_A-COMP-AIRCOM_01 | SSE-GUNUNG KEMBANG-AIR COMPRESSOR #01 | KM-A01A09001 | ELMOT mfg ?? HP ?? AIRCOM DRIVER | 30/05/2014 | 30/05/2014 | Preventive Maintenance | 0 | A010-A09-201021:Gunung Kembang Electrical - A010070202 (A010070202) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070202 | ELECTRICAL | ELECTMOTOR | ELECTRIC MOTOR
| 3560142 | Rita Agustina | SSE PLANNER | 6300032011 | 41778.0002 | M3 | PM1 1500h GEN PG-A01A00002 LU#01 PGB | Essential | 06/05/2014 10:12 Rita Agustina : For Rh 28500 | HENDRO ANGGORO | L01 - SSE Electrical | 41778 | 41778.9993 |  |  |  |  | 0 |  |  |  | ELECTECH | 7300049175 |  | EP03 | Essential | PM1 1500h GEN PG-A01A00002 LU#01 PGB | EP-A01A-14-BOOST-PLNT_A-GSET-GENSET_01 | SSE-PENGABUAN-POWER PLANT-GENSET #01 | PG-A01A00002 | GENERATOR CAT SR4 POWER PLANT | 19/05/2014 | 19/05/2014 | Preventive Maintenance | 0 | A010-A14-201031:Pengabuan Power Plant - A010070203 (A010070203) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070203 | Power Plant | GENERATOR | GENERATOR
| 3560141 | Farly Gani | SSE PLANNER | 6300032003 | 41787.0003 | M3 | SERV PUMP IR4x10CS6G-A01A05035 WIP7 JENE | Essential | 06/05/2014 10:08 Rita Agustina : For Rh 46K | ABDUL KADIR | M03 - SSE Pump | 41787 | 41789.9993 |  |  |  |  | 0 |  |  |  | PUMPMECH | 7300049173 |  | EP03 | Essential | SERV PUMP IR4x10CS6G-A01A05035 WIP7 JENE | EP-A01A-05-FLSTA-PUMP_A-PUMP-WIPUMP_07 | SSE-JENE-WATER INJECTION PUMP #07 | G-A01A05035 | PUMP IR 4x10CS-6 WATER INJECTION | 28/05/2014 | 30/05/2014 | Preventive Maintenance | 0 | A010-A05-201111:Jene Pumping A010070206 (A010070206) | 0 | 0 | 49 | 0 | 49 | 49 | [12 empty] | A010070206 | Pump Shop | CENTRIPUMP | CENTRIFUGAL PUMP
| 3560140 | Dadang Suherlan | PIPELINE PLANNER ADMIN | 6300031977 | 41775.0002 | M3 | PIGGING P/L OIL 4" KONENG - TERAS | Essential | 06/05/2014 08:02 Dadang Suherlan : PIGGING P/L OIL 4" KONENG - TERAS | AMRAN | P02 - SSE Pipeline | 41774 | 41774.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049124 |  | EP03 | Essential | PIGGING P/L OIL 4" KONENG - TERAS | EP-A01A-20-PLINE-PPLN_A-PIPE-OILPLINE_01 | PIPE LINE OIL KONENG - TERAS 4" 26.280M |  |  | 15/05/2014 | 15/05/2014 | Preventive Maintenance | 1 | A010-A20-201201:Koneng Pipeline (OIL) A010141400 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010241400 | Pipeline - Gas
| 3560139 | Dadang Suherlan | PIPELINE PLANNER ADMIN | 6300031976 | 41779.0002 | M3 | PIGGING P/L OIL 3" LAGAN-RAMBUTAN | Essential | 06/05/2014 08:00 Dadang Suherlan : PIGGING P/L OIL 3" LAGAN-RAMBUTAN | AMRAN | P02 - SSE Pipeline | 41779 | 41780.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049120 |  | EP03 | Essential | PIGGING P/L OIL 3" LAGAN-RAMBUTAN | EP-A01A-00-PLINE-PPLN_A-PIPE-OILPLINE_01 | PIPE LINE OIL LAGAN-RAMBUTAN 3" 14.525 M |  |  | 20/05/2014 | 21/05/2014 | Preventive Maintenance | 1 | A010-A00-201201:Lagan Pipeline (OIL) A010141400 (A010141400) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010241400 | Pipeline - Gas
| 3560128 | Rison | SSE MECHANICAL ADMINISTRATION | 6400004831 | 41757.6667 | Z4 | LEAK HOSE/MOTOR OVER LOAD A.COMP#B KRMSN | Desireable | 05/05/2014 21:27 Rison : Tanggal 5 Febuari 2014 dilakukan perbaiakn hose dan trouble shooting dengan indikasi MOL (Motor Over Load), ditemukan penyebaran panas pada cooler, oil/air tidak merata akibat tidak berfungsina dengan baik parts thermostastic valve. Dari hasil inspeksi, beberapa part membutuhkan segera penggantian karena sudah hampir mencapai MTBF-nya ( hose/o-seal/ring yang rapuh, baut slek dan unit sering mati dengan indikasi MOL). | Tri Cahyono | L01 - SSE Electrical | 41757.3333 | 41757.6667 |  |  | 0 | 0 | 0 |  |  | -- select -- | MECHTECH | 7400007221 |  | EP04 | Desireable | LEAK HOSE/MOTOR OVER LOAD A.COMP#B KRMSN | EP-A01A-21-FLSTA-FLST_A-COMP-AIRCOMP_02 | SSE-KERAMASAN-AIR COMPRESSOR #02 | K-A01A21002 | COMPRESSOR mfg?? AIR SUPPLY | 41764 | 30/11/2014 | Non Plant Equipment | 1 | A010-A21-201162:Keramasan Pumping & Gauging - A010070206 (A010070206) | 0 | 12064.45 | 0 | 0 | 0 | 12064.45 | 270763 | [11 empty] | A010070206 | Pump Shop | AIRCOMPRES | AIR COMPRESSOR
| 3559717 | Farly Gani | SSE PLANNER | 6300031973 | 41785.0003 | M3 | 1000H OBTAIN ENGINE LUBEOIL GENSET#1 GKB | Essential | 05/05/2014 16:04 Farly Gani : for rh 56000 | EKO YULIANTO | M01 - SSE Mechanical | 41785 | 41785.9993 |  |  |  |  | 0 |  |  |  | MECHTECH | 7300049237 |  | EP03 | Essential | 1000H OBTAIN ENGINE LUBEOIL GENSET#1 GKB | EP-A01A-09-PPLNT-PLNT_A-GSET-GENSET_01 | SSE-GUNUNG KEMBANG-GENERATOR SET #01 | PE-A01A06004 | ENGINE CAT G3508 GENERATOR DRIVER | 26/05/2014 | 26/05/2014 | Inspection | 1 | A010-A09-201031:Gunung Kembang Power Plant (A010070203) | 0 | 0 | 15.95 | 0 | 15.95 | 15.95 | [12 empty] | A010070203 | Power Plant | GASENGINE | GAS ENGINE
| 3559715 | Farly Gani | SSE PLANNER | 6300031974 | 41785.0003 | M3 | 1000H OBTAIN ENGINE LUBEOIL GENSET#6 JEN | Essential | 05/05/2014 16:06 Farly Gani : for rh 44500 | EKO YULIANTO | M01 - SSE Mechanical | 41785 | 41785.9993 |  |  |  |  | 0 |  |  |  | MECHTECH | 7300049236 |  | EP03 | Essential | 1000H OBTAIN ENGINE LUBEOIL GENSET#6 JEN | EP-A01A-05-PPLNT-PLNT_A-GSET-GENSET_06 | SSE-JENE-GENERATOR SET #06 | PE-A01A05008 | ENGINE CAT G3516 GENERATOR DRIVER | 26/05/2014 | 26/05/2014 | Inspection | 1 | A010-A05-201030:Jene Power Plant A010070203 (A010070203) | 0 | 0 | 15.95 | 0 | 15.95 | 15.95 | [12 empty] | A010070203 | Power Plant | GASENGINE | GAS ENGINE
| 3559714 | Farly Gani | SSE PLANNER | 6300031971 | 41782.0003 | M3 | 1000H OBTAIN ENGINE LUBEOIL GENSET#5 JEN | Essential | 05/05/2014 16:08 Farly Gani : for rh 44500 | EKO YULIANTO | M01 - SSE Mechanical | 41782 | 41782.9993 |  |  |  |  | 0 |  |  |  | MECHTECH | 7300049235 |  | EP03 | Essential | 1000H OBTAIN ENGINE LUBEOIL GENSET#5 JEN | EP-A01A-05-PPLNT-PLNT_A-GSET-GENSET_05 | SSE-JENE-GENERATOR SET #05 | PE-A01A05007 | ENGINE CAT G3516 GENERATOR DRIVER | 23/05/2014 | 23/05/2014 | Inspection | 1 | A010-A05-201030:Jene Power Plant A010070203 (A010070203) | 0 | 0 | 15.95 | 0 | 15.95 | 15.95 | [12 empty] | A010070203 | Power Plant | GASENGINE | GAS ENGINE
| 3559713 | Farly Gani | SSE PLANNER | 6300031970 | 41782.0003 | M3 | 1000H OBTAIN ENGINE LUBE OIL COMP#4 TRS | Essential | 05/05/2014 16:09 Farly Gani : for rh 67000 | EKO YULIANTO | M01 - SSE Mechanical | 41782 | 41782.9993 |  |  |  |  | 0 |  |  |  | MECHTECH | 7300049234 |  | EP03 | Essential | 1000H OBTAIN ENGINE LUBE OIL COMP#4 TRS | EP-A01A-03-GPLNT-GPLN_A-COMP-GASCOM_04 | SSE-TERAS-GAS PLANT#A-GAS COMPRESSOR #04 | KE-A01A03006 | ENGINE CAT G3512 COMPRESSOR DRIVER | 23/05/2014 | 23/05/2014 | Inspection | 1 | A010-A03-201152:Teras Gas Compression (A010241000) | 0 | 0 | 15.95 | 0 | 15.95 | 15.95 | [12 empty] | A010241000 | Sep/Deh.Plant - Gas | GASENGINE | GAS ENGINE
| 3559705 | Farly Gani | SSE PLANNER | [14 empty] | 0 |  |  |  |  | 7300047965 |  | EP03 | Essential | 1500h G398 KE-A01A02006 COMP DR#03 RBT | EP-A01A-02-GPLNT-GPLN_A-COMP-GASCOM_03 | SSE-RAMBUTAN-GAS PLANT#A-COMPRESOR #03 | KE-A01A02006 | ENGINE CAT G398 COMPRESSOR DRIVER | 23/05/2014 | 24/05/2014 | Preventive Maintenance | 0 | A010-A02-201152:Rambutan Gas Compression (A010241000) | 0 | 1051.68 | 55.35 | 0 | 55.35 | 1107.03 | [14 empty] | GASENGINE | GAS ENGINE
| 3559067 | Rita Agustina | SSE PLANNER | 6300031975 | 41610 | M3 | 4500h ARIEL JGE2 K-A01A00006#04 LGN. | Essential | 27/11/2013 15:31 RITA AGUSTINA : For Rh 13500 | EKO YULIANTO | M01 - SSE Mechanical | 41767 | 41768.9993 | 41770.4167 | 41770.7083 | 7 | 0 | 7 | Maintenance Technician | Mechanical Problem | Non Productive Time & Env | MECHTECH | 7300041583 |  | EP03 | Essential | 4500h ARIEL JGE2 K-A01A00006#04 LGN. | EP-A01A-00-GPLNT-GPLN_A-COMP-GASCOM_04 | SSE-LAGAN-GAS PLANT#A-GAS COMPRESSOR #04 | K-A01A00006 | GAS COMPRESSOR ARIEL JGE2 #4GAS SALES | 41856 | 41887 | Preventive Maintenance | 0 | A010-A00-201152:Lagan Gas Compression (A010241000) | 2505.94 | 2527.38 | 1044.7 | 0 | 3550.64 | 3572.08 | 237644 |  | LUBE, OFLT | Lube Oil, Oil Filter | NDMG, NDMG | No Damage, No Damage | COTH, COTH | Other (explain in text), Other (explain in text) | REPL, REPL | Replacing, Replacing |  |  | A010241000 | Sep/Deh.Plant - Gas | GASCOMPRES | GAS COMPRESSOR
| 3557743 | Rison | SSE MECHANICAL ADMINISTRATION | 6100017518 | 41760.7083 | M1 | EJW & EOT HIGH TEMPERARTURE COMP#04 GKM | Urgent | 02/05/2014 15:59 Rison : Ditemukan EJW : 208 F, EOT: 221 F. Dilakukan cleaning heat exchanger dan oil cooler. Setelah cleaning di dapat EJW: 187F dan EOT 185F. | A.Fikri | M01 - SSE Mechanical | 41759.4167 | 41760.7083 | 41759.4167 | 41760.7083 | 31 | 0 | 31 | Maintenance Technician | Abnormal Temperature | Non Productive Time & Env | MECHTECH | 7100015538 |  | EP01 | Urgent | EJW & EOT HIGH TEMPERARTURE COMP#04 GKM | EP-A01A-09-GPLNT-GPLN_A-COMP-GASCOM_04 | SSE-GUNUNG KEMBANG-GAS COMPRESSOR #04 | KE-A01A20001 | ENGINE CAT G3516 COMPRESSOR DRIVER | 41675 | 41764 | Corrective | 0 | A010-A09-201152:Gunung Kembang Gas Compression (A010241000) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | FFAN, FFAN | FinFan, FinFan | DIRT, DIRT | Dirty (Kotor), Dirty (Kotor) | COOD, COOD | Operation Beyond Design, Operation Beyond Design | CLEN, CLEN | Cleaning, Cleaning |  |  | A010241000 | Sep/Deh.Plant - Gas | GASENGINE | GAS ENGINE
| 3557530 | Rison | SSE MECHANICAL ADMINISTRATION | 6100017482 | 41760.4583 | M1 | REPAIR G-342 CTP#2 G.KEMBANG | Essential | 02/05/2014 14:25 Rison : Temuan : low power - RPM 750. Dilakukan check spark plug, check fuel dan adjust power screw Ok. | A.Fikri | M01 - SSE Mechanical | 41760.4167 | 41760.4583 | 41760.4167 | 41760.4583 | 1 | 0 | 1 | Personal on duty (operator/checker) | Abnormal Power | Non Productive Time & Env | MECHTECH | 7100015502 |  | EP01 | Essential | REPAIR G-342 CTP#2 G.KEMBANG | EP-A01A-09-FLSTA-PUMP_A-PUMP-CTPUMP_02 | SSE-G. KEMBANG-CRUDE TRANSFER PUMP #02 | GE-A01A06003 | ENGINE CAT G342 CTP DRIVER | 41675 | 41764 | Corrective | 0 | A010-A09-201111:Gunung Kembang Pumping A010070206 (A010070206) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CBRT | Carburator | NDMG | No Damage | COTH | Other (explain in text) | ADJS | Adjust | 3560385 | 41765 | A010070206 | Pump Shop | GASENGINE | GAS ENGINE
| 3556330 | Nurkholis | SSE MECHANIC ADMINISTRATION | 6100017473 | 41760.375 | M1 | COMP 02 SOKA CYL 5 HIGH TEMP | Emergency | 01/05/2014 10:39 Nurkholis : Dilakukan stop normal pada unit comp. 2 soka untuk perbaikkan cyl 5 high temperature intermitent. Ditemukan koneksi pada panel junction box cyl 5 thermocouple kendor. Action: dilakukan pengencangan kembali koneksi kabel. Unit run load kembali Done by: Africo | AFRICO | M01 - SSE Mechanical | 41753.5833 | 41753.5938 | 41753.5833 | 41753.5938 | 0 | 15 | 0.25 | Maintenance Technician | Electrical Problem | Prod. Loss & Safety | MECHTECH | 7100015493 |  | EP01 | Emergency | COMP 02 SOKA CYL 5 HIGH TEMP | EP-A01A-06-GPLNT-GPLN_A-COMP-GASCOM_02 | SSE-SOKA-GAS PLANT#A-GAS COMPRESSOR #02 | KE-A01A06002 | ENGINE CAT G3516 COMPRESSOR DRIVER | 41644 | 41646 | Corrective | 0 | A010-A06-201152:Soka Gas Compression (A010241000) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CABL | Cable | SHCR | Short-Circuited | CMMC | Lack of Maintenance Control | RPAI | Repairing |  |  | A010241000 | Sep/Deh.Plant - Gas | GASENGINE | GAS ENGINE
| 3556025 | Opry | SSE MECHANICAL ADMINISTRATION | 6100017483 | 41759.6667 | M1 | COMPRESSOR 4 SOKA UNDER SPEED | Urgent | 30/04/2014 16:44 Opry : Tgl 28 April 2014 pukul 11.00 unit Comp. 04 Soka distop normal untuk dilakukan pemeriksaan lubrication valve mechanism camshaft. Ditemukan kondisi camshaft lube masih bagus, kondisi push rod cyl 3,4,6,8,9,11,13 pelumasan kering, dilakukan test run dengan kondisi cover valve dibuka, ground transformer dijumper ke body ditemukan pada rocker arm cyl 2,6,8,9,11,13 oli tidak memercik ke push rod. Dilakukan penggantian rocker arm cyl 3,6,8,9,11,13 dengan rocker arm cyl 1-6 gas comp 6 Lagan Unit dilakukan run load pada pukul 00.15 tgl 29 April 2014. Done by: Africo, Paramartha, Erwin | AFRICO | M01 - SSE Mechanical | 41757.4583 | 41758.0104 | 41757.4583 | 41758.0104 | 13 | 15 | 13.25 | Maintenance Technician | Lubrication Degradation | Prod. Loss & Safety | MECHTECH | 7100015503 |  | EP01 | Urgent | COMPRESSOR 4 SOKA UNDER SPEED | EP-A01A-06-GPLNT-GPLN_A-COMP-GASCOM_04 | SSE-SOKA-GAS PLANT#A-GAS COMPRESSOR #04 | KE-A04A09032 | ENGINE CAT G3516 GAS COMPRESSOR DRIVER | 28/04/2014 | 28/07/2014 | Corrective | 0 | A010-A06-201152:Soka Gas Compression (A010241000) | 0 | 0 | 4696.02 | 0 | 4696.02 | 4696.02 |  |  | CYHD | Cylinder Head | WORN | Worn Out (Aus) | COOD | Operation Beyond Design | REPL | Replacing |  |  | A010241000 | Sep/Deh.Plant - Gas | GASENGINE | GAS ENGINE
| 3555527 | Opry | SSE MECHANICAL ADMINISTRATION | 6200004163 | 41759.3958 | M2 | DETONATION SHUTDOWN GENSET 06 JENE | Urgent | 30/04/2014 11:08 Opry : Terjadi breakdown pada tanggal 26 April 2014 pukul 19.00 dengan indikasi detonation shutdown. Ditemukan spark plug cyl 3 air gap renggang, transformer cyl 10 short circuit pada dioda. Dilakukan cleaning all spark plug and regap, replace transformer cyl 10, replace left hand detonasi sensor, check regulator kondisi bersih. Unit run load tanggal 27 April 2014 pukul 17.00, RPM 1200, 60 Hz, EOP 60 Psi, EJW 198 F, load 550 KW, voltage 471 V done by: Africo, Hendrajaya | AFRICO | M01 - SSE Mechanical | 41755.7917 | 41756.7083 | 41755.7917 | 41756.7083 | 22 | 0 | 22 | Maintenance Technician | Electrical Problem | Prod. Loss & Environment | MECHTECH | 7200005844 |  | EP02 | Urgent | DETONATION SHUTDOWN GENSET 06 JENE | EP-A01A-05-PPLNT-PLNT_A-GSET-GENSET_06 | SSE-JENE-GENERATOR SET #06 | PE-A01A05008 | ENGINE CAT G3516 GENERATOR DRIVER | 30/04/2014 | 30/08/2014 | Breakdown | 0 | A010-A05-201030:Jene Power Plant A010070203 (A010070203) | 0 | 0 | 771.11 | 0 | 771.11 | 771.11 |  |  | SNSR | Sensor for Speed and Timing | SHCR | Short-Circuited | CMLT | Design Life Time of material | REPL | Replacing |  |  | A010070203 | Power Plant | GASENGINE | GAS ENGINE
| 3554732 | Opry | SSE MECHANICAL ADMINISTRATION | 6100017472 | 41758.5938 | M1 | TRIAL GOVERNOUR & ACTUATOR ELECTRIC | Emergency | 29/04/2014 15:28 Opry : Dilakukan trial governour & actuator electric pada unit LU 03 Rambutan untuk mengontrol speed pada engine. Action: - instal actuator dan governour - instal MPU Dilakukan test dan adjusting Dilakukan test run iddle RPM 1400 status ok Dilakukan test run load RPM 1800 status ok Done by: Paramartha BW | PARAMARTHA | M01 - SSE Mechanical | 41745.4583 | 41745.625 | 41745.4583 | 41745.625 | 4 | 0 | 4 | Maintenance Technician | Electrical Problem | Prod. Loss & Safety | MECHTECH | 7100015492 |  | EP01 | Emergency | TRIAL GOVERNOUR & ACTUATOR ELECTRIC | EP-A01A-02-PPLNT-PLNT_A-GSET-GENSET_03 | SSE-RAMBUTAN-GENERATOR SET #03 | PE-A01A04002 | ENGINE CAT G3408 SPARE | 16/04/2014 | 16/07/2014 | Corrective | 0 | A010-A02-201030:Rambutan Power Plant A010070203 (A010070203) | 0 | 0 | 150.05 | 0 | 150.05 | 150.05 |  |  | ACTR | Actuator | NDMG | No Damage | COTH | Other (explain in text) | TEST | Testing |  |  | A010070203 | Power Plant | GASENGINE | GAS ENGINE
| 3554392 | Farly Gani | SSE PLANNER | 6300031815 | 41782.0003 | M3 | PM1 1500h GEN PG-A01A03001 LU#02 SERDANG | Essential | 29/04/2014 13:47 Farly Gani : for rh 45000 | M. BAZARUL AQSHA | L01 - SSE Electrical | 41782 | 41782.9993 |  |  |  |  | 0 |  |  |  | ELECTECH | 7300049103 |  | EP03 | Essential | PM1 1500h GEN PG-A01A03001 LU#02 SERDANG | EP-A01A-04-BOOST-BOOS_A-GSET-GENSET_02 | SSE-SERDANG-GENERATOR SET #02 | PG-A01A03001 | GENERATOR CAT SR4 POWER PLANT | 23/05/2014 | 23/05/2014 | Preventive Maintenance | 0 | A010-A04-201031:Serdang Power Plant A010070203 (A010070203) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070203 | Power Plant | GENERATOR | GENERATOR
| 3554391 | Ugeng Rusdiyanto | PLANNER OF DRILLING FIELD SUPPORT | 6300031895 | 41761 | M3 | PM ENGINE CAT D3406 PE-A01A06006 -DRL | Essential | 29/04/2014 14:38 Ugeng Rusdiyanto : PM 2 750 HR (RH = 14.250) ENGINE CAT D3406, engine genset silent no.2 Emsco Rig, S/N : 1DZ04033, RH = 14.116 per tanggal 29 April 2014. | FEBRIANSYAH | D01 - SSE Drilling | 41761 | 41767.9993 |  |  |  |  | 0 |  |  |  | DRILTECH | 7300049092 |  | EP03 | Essential | PM ENGINE CAT D3406 PE-A01A06006 -DRL | EP-A01A-06-DRILL-RIGG_A-GSET-SILENT_02 | SSE-SOKA-EMSCO-POWER PLANT-SILENT #02 | PE-A01A06006 | ENGINE CAT D3406 DI GENERATOR DRIVER | 41675 | 41856 | Preventive Maintenance | 1 | A010-A06-205170:Soka Drilling Rig Emsco A010060310 ( A010060310 ) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010060310 | Rig Emsco | DISLENGINE | DIESEL ENGINE
| 3554390 | Ugeng Rusdiyanto | PLANNER OF DRILLING FIELD SUPPORT | 6300031897 | 41762 | M3 | PM ENGINE CAT D3406 PE-A01A06005 -DRL | Essential | 29/04/2014 14:34 Ugeng Rusdiyanto : PM 4 1500 HR (RH = 12.000) ENGINE CAT D3406, engine genset silent no.1 Emsco Rig, S/N : 1DZ706087, RH = 11.885 per tanggal 29 April 2014. | FEBRIANSYAH | D01 - SSE Drilling | 41762 | 41768.9993 |  |  |  |  | 0 |  |  |  | DRILTECH | 7300049091 |  | EP03 | Essential | PM ENGINE CAT D3406 PE-A01A06005 -DRL | EP-A01A-06-DRILL-RIGG_A-GSET-SILENT_01 | SSE-SOKA-EMSCO-POWER PLANT-SILENT #01 | PE-A01A06005 | ENGINE CAT D3406 DI GENERATOR DRIVER | 41703 | 41887 | Preventive Maintenance | 1 | A010-A06-205170:Soka Drilling Rig Emsco A010060310 ( A010060310 ) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010060310 | Rig Emsco | DISLENGINE | DIESEL ENGINE
| 3554389 | Ugeng Rusdiyanto | PLANNER OF DRILLING FIELD SUPPORT | 6300031896 | 41761 | M3 | PM ENGINE CAT D3406 HE-A04A09033 -DRL | Essential | 29/04/2014 14:28 Ugeng Rusdiyanto : PM 2 750 HR (RH = 6.750) ENGINE CAT D3406, engine Rig no.2 Emsco Rig, S/N : 2WB03430, RH = 6.638 per tanggal 29 April 2014. | FEBRIANSYAH | D01 - SSE Drilling | 41761 | 41767.9993 |  |  |  |  | 0 |  |  |  | DRILTECH | 7300049090 |  | EP03 | Essential | PM ENGINE CAT D3406 HE-A04A09033 -DRL | EP-A01A-06-DRILL-RIGG_A-MOBL-ENGINE_02 | SSE-SOKA-EMSCO-MOBILE-ENGINE #02 | HE-A04A09033 | ENGINE CAT D3406 MOBILE DRIVER | 41675 | 41856 | Preventive Maintenance | 1 | A010-A06-205170:Soka Drilling Rig Emsco A010060310 ( A010060310 ) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010060310 | Rig Emsco | DISLENGINE | DIESEL ENGINE
| 3554388 | Ugeng Rusdiyanto | PLANNER OF DRILLING FIELD SUPPORT | 6300031898 | 41761 | M3 | PM ENGINE CAT D3512 GE-A01A06008 -DRL | Essential | 29/04/2014 14:21 Ugeng Rusdiyanto : PM 1 250 HR (RH = 1750) ENGINE CAT D3512, engine Mud Pump no 2 Emsco Rig, S/N : 85Z01908, RH = 1.609 per 29 April 2014. | FEBRIANSYAH | D01 - SSE Drilling | 41761 | 41767.9993 |  |  |  |  | 0 |  |  |  | DRILTECH | 7300049089 |  | EP03 | Essential | PM ENGINE CAT D3512 GE-A01A06008 -DRL | EP-A01A-06-DRILL-RIGG_A-PUMP-MDPUMP_02 | SSE-SOKA-EMSCO-MUD-PUMP #02 | GE-A01A06008 | ENGINE CAT D3512 TA PUMP DRIVER | 41675 | 41856 | Preventive Maintenance | 1 | A010-A06-205170:Soka Drilling Rig Emsco A010060310 ( A010060310 ) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010060310 | Rig Emsco | DISLENGINE | DIESEL ENGINE
| 3554387 | Rita Agustina | SSE PLANNER | [14 empty] | 0 |  |  |  |  | 7300049078 |  | EP03 | Essential | 9000h G3516 KE-A01A20002 COMP 02 KONENG | EP-A01A-20-GPLNT-GPLN_A-COMP-GASCOM_02 | SSE-KONENG-GASPLANT_A-GAS COMPRESSOR #02 | KE-A01A20002 | ENGINE CAT G3516 COMPRESSOR DRIVER | 22/05/2014 | 24/05/2014 | Preventive Maintenance | 0 | A010-A20-201152:Koneng Gas Compression - A010241000 (A010241000) | 0 | 0 | 4374.67 | 0 | 4374.67 | 4374.67 | [14 empty] | GASENGINE | GAS ENGINE
| 3554386 | Farly Gani | SSE PLANNER | 6300031899 | 41785.0003 | M3 | 750h G3306 GE-A01A06001 GENSET#01 IBUL. | Essential | 29/04/2014 14:17 Farly Gani : for rh 55500 | FITRIADI MASO | M01 - SSE Mechanical | 41785 | 41787.9993 |  |  |  |  | 0 |  |  |  | MECHTECH | 7300049071 |  | EP03 | Essential | 750h G3306 GE-A01A06001 GENSET#01 IBUL. | EP-A01A-01-PPLNT-PLNT_A-GSET-GENSET_01 | SSE-IBUL-GENERATOR SET #01 | GE-A01A06001 | ENGINE CAT G3306 GENERATOR DRIVER | 26/05/2014 | 28/05/2014 | Preventive Maintenance | 0 | A010-A01-201031:Ibul Power Plant A010070203 (A010070203) | 0 | 0 | 519.21 | 0 | 519.21 | 519.21 | [12 empty] | A010070203 | Power Plant | GASENGINE | GAS ENGINE
| 3554385 | Farly Gani | SSE PLANNER | [14 empty] | 0 |  |  |  |  | 7300049069 |  | EP03 | Essential | 1500h G3512 KE-A01A09002 COMP #01 GKM. | EP-A01A-09-GPLNT-GPLN_A-COMP-GASCOM_01 | SSE-GUNUNG KEMBANG-GAS COMPRESSOR #01 | KE-A01A09002 | ENGINE CAT G3512 COMPRESSOR DRIVER | 20/05/2014 | 21/05/2014 | Preventive Maintenance | 0 | A010-A09-201152:Gunung Kembang Gas Compression (A010241000) | 0 | 953.28 | 145.5 | 0 | 145.5 | 1098.78 | [14 empty] | GASENGINE | GAS ENGINE
| 3554384 | Farly Gani | SSE PLANNER | [14 empty] | 0 |  |  |  |  | 7300049068 |  | EP03 | Essential | 9000h G3512 KE-A01A02008 COMP #05 RBT. | EP-A01A-02-GPLNT-GPLN_A-COMP-GASCOM_05 | SSE-RAMBUTAN-GAS PLANT#A-COMPRESOR #05 | KE-A01A02008 | ENGINE CAT G3512 COMPRESSOR DRIVER | 20/05/2014 | 22/05/2014 | Preventive Maintenance | 0 | A010-A02-201152:Rambutan Gas Compression (A010241000) | 0 | 1016.64 | 2292.79 | 0 | 2292.79 | 3309.43 | [14 empty] | GASENGINE | GAS ENGINE
| 3554383 | Farly Gani | SSE PLANNER | [14 empty] | 0 |  |  |  |  | 7300049067 |  | EP03 | Essential | 4500h G3512 KE-A01A00001 COMP#1 LGN. | EP-A01A-00-GPLNT-GPLN_A-COMP-GASCOM_01 | SSE-LAGAN-GAS PLANT#A-GAS COMPRESSOR #01 | KE-A01A00001 | ENGINE CAT G3512 COMPRESSOR DRIVER | 25/05/2014 | 26/05/2014 | Preventive Maintenance | 0 | A010-A00-201152:Lagan Gas Compression (A010241000) | 0 | 953.28 | 2326.27 | 0 | 2326.27 | 3279.55 | [14 empty] | GASENGINE | GAS ENGINE
| 3554382 | Farly Gani | SSE PLANNER | 6300031900 | 41772.0002 | M3 | 1000H OBTAIN ENGINE LUBEOIL GENSET#3 JEN | Essential | 29/04/2014 14:42 Farly Gani : for rh 23500 | FITRIADI MASO | M01 - SSE Mechanical | 41772 | 41772.9993 | 1/1/1753 12:00:00 AM | 1/1/1753 12:00:00 AM | 0 | 0 | 0 | Maintenance Technician | Mechanical Problem | No effect | MECHTECH | 7300048650 |  | EP03 | Essential | 1000H OBTAIN ENGINE LUBEOIL GENSET#3 JEN | EP-A01A-05-PPLNT-PLNT_A-GSET-GENSET_03 | SSE-JENE-GENERATOR SET #03 | PE-A01A09004 | ENGINE CAT G3512 GENERATOR DRIVER | 13/05/2014 | 13/05/2014 | Inspection | 1 | A010-A05-201030:Jene Power Plant A010070203 (A010070203) | 0 | 0 | 15.95 | 0 | 15.95 | 15.95 |  |  | LUBE | Lube Oil | NDMG | No Damage | COTH | Other (explain in text) | TEST | Testing | 3563228 | 41767 | A010070203 | Power Plant | GASENGINE | GAS ENGINE
| 3554381 | Farly Gani | SSE PLANNER | 6300031816 | 41779.0002 | M3 | PM1 2K PUMP ELMOTGM-A01A05024 PIT1JENE | Essential | 29/04/2014 14:45 Farly Gani : PM1 2K PUMP ELMOTGM-A01A05024 PIT1JENE | M. BAZARUL AQSHA | L01 - SSE Electrical | 41779 | 41779.9993 | 1/1/1753 12:00:00 AM | 1/1/1753 12:00:00 AM | 0 | 0 | 0 | Maintenance Technician | No Symptom (EP03 Only) | No effect | ELECTECH | 7300048439 |  | EP03 | Essential | PM1 2K PUMP ELMOTGM-A01A05024 PIT1JENE | EP-A01A-05-FLSTA-PUMP_A-PUMP-SPPUMP_01 | SSE-JENE-SKIMMING PIT PUMP #01 | GM-A01A05024 | ELMOT SIEMEN 40 HP CTP DRIVER | 20/05/2014 | 20/05/2014 | Preventive Maintenance | 1 | A010-A05-201020:Jene Electrical - A010070202 (A010070202) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | MOTR | Motor | NDMG | No Damage | COTH | Other (explain in text) | CHEK | Checking |  |  | A010070202 | ELECTRICAL | ELECTMOTOR | ELECTRIC MOTOR
| 3554357 | Opry | SSE PUMP & DIESEL SHOP ADMINISTRATION | 6400004832 | 41723.3333 | Z4 | GOH ENGINE GM 8V-71 IDECO V DI JENE | Desireable | 29/04/2014 11:34 Opry : Dilakukan GOH Engine GM 8V-71 IDECO V DI JENE pada tanggal 25 Maret - 10 April 2014 di Yard Jene,karena engine low power dan banyak kebocoran oil pada engine.Dilakukan pembelian part untuk kebutuhan GOH. Status unit ok setelah GOH.Done by bey,salim,yoyo,edison,ang,mei | Bambang EY | M02 - SSE Diesel & Rig | 41723.3333 | 41739.6667 |  |  | 0 | 0 | 0 |  |  | -- select -- | PUMPMECH | 7400007224 |  | EP04 | Desireable | GOH ENGINE GM 8V-71 IDECO V DI JENE | EP-A01A-06-WOWSS-RIGG_A-ENGN-ENGINE_01 | SSE-SOKA-IDECO_5-MOBILE-ENGINE #01 | RIG-A04A09005-E1 | ENGINE DIESEL GM 8V71 MOBILE DRIVER | 29/04/2014 | 28/10/2014 | Non Plant Equipment | 1 | A010-A06-201190:Soka WO/WS Rig A010060205 (A010060205) | 0 | 19479.31 | 0 | 0 | 0 | 19479.31 | 271112 | [11 empty] | A010060205 | WO/WS Rig | DISLENGINE | DIESEL ENGINE
| 3554009 | Opry | SSE MECHANICAL ADMINISTRATION | 6100017474 | 41758.3438 | M1 | GENSET 05 JENE HUNTING | Emergency | 29/04/2014 09:13 Opry : Dilakukan stop normal pada unit genset 05 Jene untuk perbaikkan indikasi RPM engine hunting. Ditemukan RPM hunting 1180-1210, manifold air starter pressure 140-170 kpa. Action: 1. test compressi all cylinder (170-180 Psi) 2. Clean & regap spark plug cylinder 1-16 3. Check & cleaning regulator 4. replace waste gate transformer cyl 15 dan 16 Unit run load kembali pukul 11.30, RPM 1200, EJW 198 F, EOP 62, voltage 471 V, Load 548 KW, MAP 150 kpa Done by: Africo, Bambang S, Delfion | AFRICO | M01 - SSE Mechanical | 41754.375 | 41754.4792 | 41754.375 | 41754.4792 | 2 | 30 | 2.5 | Maintenance Technician | Mechanical Problem | Prod. Loss & Safety | MECHTECH | 7100015494 |  | EP01 | Emergency | GENSET 05 JENE HUNTING | EP-A01A-05-PPLNT-PLNT_A-GSET-GENSET_05 | SSE-JENE-GENERATOR SET #05 | PE-A01A05007 | ENGINE CAT G3516 GENERATOR DRIVER | 25/04/2014 | 25/08/2014 | Corrective | 0 | A010-A05-201030:Jene Power Plant A010070203 (A010070203) | 0 | 0 | 2681.13 | 0 | 2681.13 | 2681.13 |  |  | REGT | Regulator | JAMM | Jammed (Macet) | COOD | Operation Beyond Design | REPL | Replacing |  |  | A010070203 | Power Plant | GASENGINE | GAS ENGINE
| 3553995 | Farly Gani | SSE PLANNER | 6300031821 | 41775.0002 | M3 | PM 2 9000h GEN PG-A01A03004 LU #02 TERAS | Essential | 29/04/2014 11:18 Farly Gani : for rh 54000 | M. BAZARUL AQSHA | L01 - SSE Electrical | 41775 | 41775.9993 |  |  |  |  | 0 |  |  |  | ELECTECH | 7300049073 |  | EP03 | Essential | PM 2 9000h GEN PG-A01A03004 LU #02 TERAS | EP-A01A-03-PPLNT-PLNT_A-GSET-GENSET_02 | SSE-TERAS-GENERATOR SET #02 | PG-A01A03004 | GENERATOR CAT SR4 POWER PLANT | 16/05/2014 | 16/05/2014 | Preventive Maintenance | 0 | A010-A03-201031:Teras Power Plant A010070203 (A010070203) | 0 | 0 | 324.2 | 0 | 324.2 | 324.2 | [12 empty] | A010070203 | Power Plant | GENERATOR | GENERATOR
| 3553994 | Farly Gani | SSE PLANNER | 6300031814 | 41780.0002 | M3 | PM1 2K PUMP ELMOT GM-A01A14008 FDR3 PGB. | Essential | 29/04/2014 11:20 Farly Gani : for rh 42000 | M. BAZARUL AQSHA | L01 - SSE Electrical | 41780 | 41780.9993 | 1/1/1753 12:00:00 AM | 1/1/1753 12:00:00 AM | 0 | 0 | 0 | Maintenance Technician | No Symptom (EP03 Only) | No effect | ELECTECH | 7300049072 |  | EP03 | Essential | PM1 2K PUMP ELMOT GM-A01A14008 FDR3 PGB. | EP-A01A-14-BOOST-BOOS_A-PUMP-FDPUMP_03 | SSE-PENGABUAN-FEEDER PUMP #03 | GM-A01A14008 | ELMOT mfg ?? 50 HP FEEDER DRIVER | 21/05/2014 | 21/05/2014 | Preventive Maintenance | 1 | A010-A14-201021:Pengabuan Electrical - A010070202 (A010070202) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | MOTR | Motor | NDMG | No Damage | COTH | Other (explain in text) | CHEK | Checking |  |  | A010070202 | ELECTRICAL | ELECTMOTOR | ELECTRIC MOTOR
| 3553992 | Rita Agustina | SSE PLANNER | 6300031813 | 41780.0002 | M3 | SERV PUMP GOULDS3196G-A01A14008 FDR3 PGB | Essential | 29/04/2014 10:28 Rita Agustina : FOR RH 42K | ADE ZUHENDRA | M03 - SSE Pump | 41780 | 41781.9993 |  |  |  |  | 0 |  |  |  | PUMPMECH | 7300049070 |  | EP03 | Essential | SERV PUMP GOULDS3196G-A01A14008 FDR3 PGB | EP-A01A-14-BOOST-BOOS_A-PUMP-FDPUMP_03 | SSE-PENGABUAN-FEEDER PUMP #03 | G-A01A14008 | PUMP GOULDS 3196 MT FEEDER TRANSFER | 21/05/2014 | 22/05/2014 | Preventive Maintenance | 0 | A010-A14-201111:Pengabuan Pumping & Gauging A010070206 (A010070206) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010070206 | Pump Shop | CENTRIPUMP | CENTRIFUGAL PUMP
| 3553336 | Opry | SSE MECHANICAL ADMINISTRATION | 6200004172 | 41754 | M2 | UNDER SPEED COMP #04 SOKA | Emergency | 28/04/2014 14:43 Opry : Gas Comp #04 Soka breakdown dengan indikasi pada HMI PLC Under speed dan pada DDT 325-00,detonation shutdown.Ditemukan: 1.Abnormal noise dari cylinder #4,6,8,9,10 2.Adjuster screw exhaust cylinder #4,6,8,9,10 sudah aus. 3.Shut Off valve pneumatic tidak berfungsi. Dilakukan: 1.Penggantian adjuster screw cylinder #4,6,8,9,10 2.Re adjust valve lash cylinder #4,6,8,9,10 Replace shut off valve pneumatic dengan electric shut off valve.Unit Run Load jam 20.45 WIB.done by aco,dln,erw | Africo | M01 - SSE Mechanical | 41754.4236 | 41754.8646 | 41754.4243 | 41754.8646 | 10 | 34 | 10.5667 | Personal on duty (operator/checker) | Mechanical Problem | Non Productive Time & Env | MECHTECH | 7200005845 |  | EP02 | Emergency | UNDER SPEED COMP #04 SOKA | EP-A01A-06-GPLNT-GPLN_A-COMP-GASCOM_04 | SSE-SOKA-GAS PLANT#A-GAS COMPRESSOR #04 | KE-A04A09032 | ENGINE CAT G3516 GAS COMPRESSOR DRIVER | 25/04/2014 | 25/04/2014 | Breakdown | 0 | A010-A06-201152:Soka Gas Compression (A010241000) | 0 | 0 | 1305.38 | 0 | 1305.38 | 1305.38 |  |  | VLVE | Valve | WORN | Worn Out (Aus) | CMLT | Design Life Time of material | REPL | Replacing | 3560490 | 41765 | A010241000 | Sep/Deh.Plant - Gas | GASENGINE | GAS ENGINE
| 3553263 | Opry | SSE PUMP & DIESEL SHOP ADMINISTRATION | 6100017467 | 41757.5625 | M1 | ENGINE FIREHYDRANT 01 GKM NO START | Emergency | 28/04/2014 14:12 Opry : Engine fire hydrant 01 G. Kembang tidak bisa distart. Dilakukan pengecekan ditemukan battery 2 ea yg terinstal diunit sudah rusak. Dilakukan replacing battery 2 ea, setelah itu dilakukan test ditemukan engine ga mau running. Dilakukan pengecekan ditemukan rellay start tidak mau menjumper 24 volt sehingga tidak start. Baut rellay dilakukan pengejust-an. Setelah itu dilakukan test start engine, status ok. Check alternator status ok (voltage: 13,7 V) Done by: Bambang EY, Sujantoro | BAMBANG EY | M03 - SSE Pump | 41698.4583 | 41698.5833 | 41698.4583 | 41698.5833 | 3 | 0 | 3 | Maintenance Technician | Electrical Problem | Prod. Loss & Safety | PUMPMECH | 7100015487 |  | EP01 | Emergency | ENGINE FIREHYDRANT 01 GKM NO START | EP-A01A-09-FLSTA-PUMP_A-PUMP-FRPUMP_01 | SSE-G.KEMBANG-FIRE PUMP #01 | GE-A01A09003 | ENGINE VM MTR 59A-12883 FIRE PUMP DRIVER | 28/02/2014 | 28/06/2014 | Corrective | 0 | A010-A09-201111:Gunung Kembang Pumping A010070206 (A010070206) | 0 | 0 | 792.88 | 0 | 792.88 | 792.88 |  |  | ESYS | Electrical Control System | NDMG | No Damage | CMLT | Design Life Time of material | REPL | Replacing |  |  | A010070206 | Pump Shop | DISLENGINE | DIESEL ENGINE
| 3553235 | Opry | SSE MECHANICAL ADMINISTRATION | 6200004173 | 41751 | M2 | UNDER SPEED COMP #04 SOKA | Emergency | 28/04/2014 14:02 Opry : Tanggal 22 April 2014 jam 00.00 WIB unit down dengan indikasi underspeed.Pada DDT muncul indikasi 32500 detonation shutdown .Temuan: 1.MAT saat malam hari 34Â°F sangat rendah.by pass di thermostat tidak ada. 2.Timing Actual 24Â°,desire 30Â°. 3.Detonation level 3-4 Bar 4.Vibrasi tinggi pada cylinder 1,3,4,8,9,10,13,ditemukan push rod 4,8,9,10 aus. Action: 1.Cek regulator fuel & filter besih dan ok 2.Adjust air fuel ratio 3.replace push rodyang aus cylinder 4,8,9,10 4.valve Lash cylinder 1,3,4,8,9,10,13 Unit run load pukul 15.00 WIB.line by pass dan thermostat akan diorder.done by aco,nda | Africo | M01 - SSE Mechanical | 41751 | 41751.625 | 41751 | 41751.625 | 15 | 0 | 15 | Personal on duty (operator/checker) | Abnormal Vibration | Non Productive Time & Env | MECHTECH | 7200005846 |  | EP02 | Emergency | UNDER SPEED COMP #04 SOKA | EP-A01A-06-GPLNT-GPLN_A-COMP-GASCOM_04 | SSE-SOKA-GAS PLANT#A-GAS COMPRESSOR #04 | KE-A04A09032 | ENGINE CAT G3516 GAS COMPRESSOR DRIVER | 28/04/2014 | 41917 | Breakdown | 0 | A010-A06-201152:Soka Gas Compression (A010241000) | 0 | 0 | 83.2 | 0 | 83.2 | 83.2 |  |  | RODD | Rod | WORN | Worn Out (Aus) | COOD | Operation Beyond Design | REPL | Replacing |  |  | A010241000 | Sep/Deh.Plant - Gas | GASENGINE | GAS ENGINE
| 3552797 | Opry | SSE PUMP & DIESEL SHOP ADMINISTRATION | 6100017509 | 41757.375 | M1 | BOCOR OIL SEAL CTP 3 TERAS | Emergency | 28/04/2014 09:31 Opry : Terjadi kebocoran pada unit CTP 3 Teras. Kebocoran terjadi pada oil seal bagian DE. Action: replace oil seal Dilakukan test ternyata tidak terdapat kebocoran lagi. status unit ok Done by: Paryono, Susanto | PARYONO | M03 - SSE Pump | 41651.4583 | 41651.625 | 41651.4583 | 41651.625 | 4 | 0 | 4 | Maintenance Technician | Leakage | Prod. Loss & Safety | PUMPMECH | 7100015529 |  | EP01 | Emergency | BOCOR OIL SEAL CTP 3 TERAS | EP-A01A-03-FLSTA-PUMP_A-PUMP-CTPUMP_03 | SSE-TERAS-CRUDE TRANSFER PUMP #03 | G-A01A03006 | PUMP RUHPUMPEN CPP-211 CRUDE TRANSFER | 41974 | 41979 | Corrective | 0 | A010-A03-201111:Teras Pumping A010070206 (A010070206) | 0 | 0 | 66 | 0 | 66 | 66 |  |  | OSEL | Oil Seal | LEAK | Leak (Bocor) | COOD | Operation Beyond Design | REPL | Replacing |  |  | A010070206 | Pump Shop | CENTRIPUMP | CENTRIFUGAL PUMP
| 3552726 | Agus Salim | PIPELINE PLANNER ADMIN | 6300031918 | 41789.0003 | M3 | PIGGING P/L OIL 4" RAMBUTAN-TERAS | Essential |  | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41789 | 41789.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049066 |  | EP03 | Essential | PIGGING P/L OIL 4" RAMBUTAN-TERAS | EP-A01A-02-PLINE-PPLN_A-PIPE-OILPLINE_01 | PIPE LINE OIL RBT - TERAS 4" 25.000M |  |  | 30/05/2014 | 30/05/2014 | Preventive Maintenance | 1 | A010-A02-201201:Rambutan Pipeline (OIL) A010141400 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010141400 | Pipeline - Oil
| 3552725 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031871 | 41782.0003 | M3 | PIGGING P/L OIL 4" RAMBUTAN-TERAS | Essential | 29/04/2014 16:51 Heri Sujono : PIGGING P/L OIL 4" RAMBUTAN-TERAS | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41782 | 41782.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049065 |  | EP03 | Essential | PIGGING P/L OIL 4" RAMBUTAN-TERAS | EP-A01A-02-PLINE-PPLN_A-PIPE-OILPLINE_01 | PIPE LINE OIL RBT - TERAS 4" 25.000M |  |  | 23/05/2014 | 23/05/2014 | Preventive Maintenance | 1 | A010-A02-201201:Rambutan Pipeline (OIL) A010141400 (A010141400) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010141400 | Pipeline - Oil
| 3552724 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031850 | 41776.0002 | M3 | PIGGING P/L OIL 4" RAMBUTAN-TERAS | Essential | 29/04/2014 14:31 Heri Sujono : PIGGING P/L OIL 4" RAMBUTAN-TERAS | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41776 | 41776.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049064 |  | EP03 | Essential | PIGGING P/L OIL 4" RAMBUTAN-TERAS | EP-A01A-02-PLINE-PPLN_A-PIPE-OILPLINE_01 | PIPE LINE OIL RBT - TERAS 4" 25.000M |  |  | 17/05/2014 | 17/05/2014 | Preventive Maintenance | 1 | A010-A02-201201:Rambutan Pipeline (OIL) A010141400 (A010141400) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010141400 | Pipeline - Oil
| 3552723 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031829 | 41770.0001 | M3 | PIGGING P/L OIL 4" RAMBUTAN-TERAS | Essential | 29/04/2014 13:43 Heri Sujono : PIGGING P/L OIL 4" RAMBUTAN-TERAS | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41770 | 41770.9993 | 1/1/1753 12:00:00 AM | 1/1/1753 12:00:00 AM | 0 | 0 | 0 | Maintenance Technician | No Symptom (EP03 Only) | No effect | PIPETECH | 7300049063 |  | EP03 | Essential | PIGGING P/L OIL 4" RAMBUTAN-TERAS | EP-A01A-02-PLINE-PPLN_A-PIPE-OILPLINE_01 | PIPE LINE OIL RBT - TERAS 4" 25.000M |  |  | 41948 | 41948 | Preventive Maintenance | 1 | A010-A02-201201:Rambutan Pipeline (OIL) A010141400 (A010141400) | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CLEN | Cleaning |  |  | A010141400 | Pipeline - Oil
| 3552722 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031802 | 41764.0001 | M3 | PIGGING P/L OIL 4" RAMBUTAN-TERAS | Essential | 29/04/2014 11:02 Heri Sujono : PIGGING P/L OIL 4" RAMBUTAN-TERAS | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41764 | 41764.9993 | 1/1/1753 12:00:00 AM | 1/1/1753 12:00:00 AM | 0 | 0 | 0 | Maintenance Technician | No Symptom (EP03 Only) | No effect | PIPETECH | 7300049062 |  | EP03 | Essential | PIGGING P/L OIL 4" RAMBUTAN-TERAS | EP-A01A-02-PLINE-PPLN_A-PIPE-OILPLINE_01 | PIPE LINE OIL RBT - TERAS 4" 25.000M |  |  | 41764 | 41764 | Preventive Maintenance | 1 | A010-A02-201201:Rambutan Pipeline (OIL) A010141400 (A010141400) | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CLEN | Cleaning |  |  | A010141400 | Pipeline - Oil
| 3552721 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031872 | 41782.0003 | M3 | PIGGING P/L OIL 4" SP6 - SP9 | Essential | 29/04/2014 16:52 Heri Sujono : PIGGING P/L OIL 4" SP6 - SP9 | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41782 | 41782.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049060 |  | EP03 | Essential | PIGGING P/L OIL 4" SP6 - SP9 | EP-A01A-06-PLINE-PPLN_A-PIPE-OILPLINE_02 | PIPE LINE OIL fr SOKA (SP6-SP9) 4" ??M |  |  | 23/05/2014 | 23/05/2014 | Preventive Maintenance | 1 | A010-A06-201201:Soka Pipeline (OIL) A010141400 (A010141400) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010141400 | Pipeline - Oil
| 3552720 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031840 | 41773.0002 | M3 | PIGGING P/L OIL 4" SP6 - SP9 | Essential | 29/04/2014 14:01 Heri Sujono : PIGGING P/L OIL 4" SP6 - SP9 | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41773 | 41773.9993 | 1/1/1753 12:00:00 AM | 1/1/1753 12:00:00 AM | 0 | 0 | 0 | Maintenance Technician | No Symptom (EP03 Only) | No effect | PIPETECH | 7300049059 |  | EP03 | Essential | PIGGING P/L OIL 4" SP6 - SP9 | EP-A01A-06-PLINE-PPLN_A-PIPE-OILPLINE_02 | PIPE LINE OIL fr SOKA (SP6-SP9) 4" ??M |  |  | 14/05/2014 | 14/05/2014 | Preventive Maintenance | 1 | A010-A06-201201:Soka Pipeline (OIL) A010141400 (A010141400) | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CLEN | Cleaning |  |  | A010141400 | Pipeline - Oil
| 3552719 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031886 | 41787.0003 | M3 | PIGGING P/L GAS 6" G.KEMBANG - SP9 | Essential | 29/04/2014 17:11 Heri Sujono : PIGGING P/L GAS 6" G.KEMBANG - SP9 | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41787 | 41787.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049058 |  | EP03 | Essential | PIGGING P/L GAS 6" G.KEMBANG - SP9 | EP-A01A-09-PLINE-PPLN_A-PIPE-GASPLINE_03 | PIPE LINE GAS G.KEMBANG - SP9 6" |  |  | 28/05/2014 | 28/05/2014 | Preventive Maintenance | 1 | A010-A09-201202:Gunung Kembang Pipeline (GAS) A010241400 (A010241400) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010241400 | Pipeline - Gas
| 3552717 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031882 | 41784.0003 | M3 | PIGGING P/L GAS 6" G.KEMBANG - SP9 | Essential | 29/04/2014 17:01 Heri Sujono : PIGGING P/L GAS 6" G.KEMBANG - SP9 | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41784 | 41784.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049057 |  | EP03 | Essential | PIGGING P/L GAS 6" G.KEMBANG - SP9 | EP-A01A-09-PLINE-PPLN_A-PIPE-GASPLINE_03 | PIPE LINE GAS G.KEMBANG - SP9 6" |  |  | 25/05/2014 | 25/05/2014 | Preventive Maintenance | 1 | A010-A09-201202:Gunung Kembang Pipeline (GAS) A010241400 (A010241400) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010241400 | Pipeline - Gas
| 3552716 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031864 | 41781.0003 | M3 | PIGGING P/L GAS 6" G.KEMBANG - SP9 | Essential | 29/04/2014 16:40 Heri Sujono : PIGGING P/L GAS 6" G.KEMBANG - SP9 | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41781 | 41781.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049056 |  | EP03 | Essential | PIGGING P/L GAS 6" G.KEMBANG - SP9 | EP-A01A-09-PLINE-PPLN_A-PIPE-GASPLINE_03 | PIPE LINE GAS G.KEMBANG - SP9 6" |  |  | 22/05/2014 | 22/05/2014 | Preventive Maintenance | 1 | A010-A09-201202:Gunung Kembang Pipeline (GAS) A010241400 (A010241400) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010241400 | Pipeline - Gas
| 3552715 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031858 | 41778.0002 | M3 | PIGGING P/L GAS 6" G.KEMBANG - SP9 | Essential | 29/04/2014 16:08 Heri Sujono : PIGGING P/L GAS 6" G.KEMBANG - SP9 | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41778 | 41778.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049055 |  | EP03 | Essential | PIGGING P/L GAS 6" G.KEMBANG - SP9 | EP-A01A-09-PLINE-PPLN_A-PIPE-GASPLINE_03 | PIPE LINE GAS G.KEMBANG - SP9 6" |  |  | 19/05/2014 | 19/05/2014 | Preventive Maintenance | 1 | A010-A09-201202:Gunung Kembang Pipeline (GAS) A010241400 (A010241400) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010241400 | Pipeline - Gas
| 3552378 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031844 | 41775.0002 | M3 | PIGGING P/L GAS 6" G.KEMBANG - SP9 | Essential | 29/04/2014 14:21 Heri Sujono : PIGGING P/L GAS 6" G.KEMBANG - SP9 | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41775 | 41775.9993 |  |  |  |  | 0 |  |  |  | PIPETECH | 7300049054 |  | EP03 | Essential | PIGGING P/L GAS 6" G.KEMBANG - SP9 | EP-A01A-09-PLINE-PPLN_A-PIPE-GASPLINE_03 | PIPE LINE GAS G.KEMBANG - SP9 6" |  |  | 16/05/2014 | 16/05/2014 | Preventive Maintenance | 1 | A010-A09-201202:Gunung Kembang Pipeline (GAS) A010241400 (A010241400) | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | A010241400 | Pipeline - Gas
| 3552377 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031837 | 41772.0002 | M3 | PIGGING P/L GAS 6" G.KEMBANG - SP9 | Essential | 29/04/2014 13:56 Heri Sujono : PIGGING P/L GAS 6" G.KEMBANG - SP9 | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41772 | 41772.9993 | 1/1/1753 12:00:00 AM | 1/1/1753 12:00:00 AM | 0 | 0 | 0 | Maintenance Technician | No Symptom (EP03 Only) | No effect | PIPETECH | 7300049053 |  | EP03 | Essential | PIGGING P/L GAS 6" G.KEMBANG - SP9 | EP-A01A-09-PLINE-PPLN_A-PIPE-GASPLINE_03 | PIPE LINE GAS G.KEMBANG - SP9 6" |  |  | 13/05/2014 | 13/05/2014 | Preventive Maintenance | 1 | A010-A09-201202:Gunung Kembang Pipeline (GAS) A010241400 (A010241400) | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CLEN | Cleaning |  |  | A010241400 | Pipeline - Gas
| 3552376 | Heri Sujono | PIPELINE PLANNER ADMIN | 6300031825 | 41769.0001 | M3 | PIPE LINE GAS G.KEMBANG - SP9 6" | Essential | 29/04/2014 11:19 Heri Sujono : PIPE LINE GAS G.KEMBANG - SP9 6" | FANI IRFAN HIDAYAT | P02 - SSE Pipeline | 41769 | 41769.9993 | 1/1/1753 12:00:00 AM | 1/1/1753 12:00:00 AM | 0 | 0 | 0 | Maintenance Technician | No Symptom (EP03 Only) | No effect | PIPETECH | 7300049052 |  | EP03 | Essential | PIPE LINE GAS G.KEMBANG - SP9 6" | EP-A01A-09-PLINE-PPLN_A-PIPE-GASPLINE_03 | PIPE LINE GAS G.KEMBANG - SP9 6" |  |  | 41917 | 41917 | Preventive Maintenance | 1 | A010-A09-201202:Gunung Kembang Pipeline (GAS) A010241400 (A010241400) | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CLEN | Cleaning |  |  | A010241400 | Pipeline - Gas